## Instructions D (hidden)
Version 1.3 6-11-2012
The Small Business Walk-through Energy Assessment Tool PROGRAM INSTRUCTIONS
This WTEA Tool is intended to be used for energy efficiency recommendations under the Small Business Program.
All projects MUST receive pre-approval before purchasing equipment or beginning work. Please review the program process and eligibility requirements on the program website as well as the Terms & Conditions on the application. Please contact the program office with any questions.
Program Process and Eligibility Requirements
Contact the Program Office |  |  | 866-353-5799
The Small Business Walkthrough Energy Assessment Report Generation Template
First, Enter Facility information on R1 Summary tab.
Second, Select measures on the "R2 Rec" tab. Be sure to include "No Cost/Low Cost" measures and check the "R2 NCLC" tab to reference measure descriptions.
Third, Enter ECM specific information:
If Lighting measures are recommended: Enter Lighting equipment in "W light exist" tab. Select lighting retrofits in "W light ECM select" tab. R2 lighting sheets (R2 T8T5, R2 CFL, R2 LED, R2 OtherLite) should populate automatically but check through them to make sure ECMs make sense. Sensors require additional input on "R2 OtherLite" tab.
If HVAC Measures are recommended: Enter HVAC information in "R2 HVAC Tune" or "R2 HVAC Repl" tabs as applicable. If HVAC sizing is unknown, enter HVAC equipment in "W HVAC" tab to estimate sizing information.
If Other Measures are recommended: Enter information on the applicable tabs (R2 Kitchen, R2 WaterHeat, R2 Vending, R2 Controls, R2 VFD, R2 Custom). Each individual measure tab has instructions as to what information is needed.
Fifth, Fill out R3 Facility Description
Sixth, Drag all unused measure tabs to the right of the R3 tab so they will not be printed.
Seventh, a) Review, revise, format for printing b) Submit for approval by designated reviewer c) Edit per reviewer feedback. d) Once approved, create PDF or paper copy to present to customer.
DelmarvaEnergyEfficiency@LMBPS.com
Measures recommended in this walk-through energy assessment are general recommendations and this report does not constitute pre-approval for installation of any equipment other than No Cost/Low Cost measures. All other measures that a customer decides to install still require a separate application form that details the specific equipment planned for installation.
Note - Please be sure to use the latest version of the application. Follow the link below to find the latest version
https://cienergyefficiency.delmarva.com/Lighting.aspx
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
Printing Instructions for Page #
Select all of the report sheets to group them together. Select print and print report. It will be automatically numbered.
Be sure to ungroup sheets after printing.
If you use an insert in the report: place the dummy tab found at the back of the template in the location where the insert will be. One dummy tab per page of insert is required.
If you need to print only one page, in order for it to have the correct page #, you must group all pages of the report, select print, then select print pages and insert the page # you wish to print. Alternatively, you can open print review, select page set up, select custom footer, delete the &{page}, and manually enter the page #

## Instructions
Version 1.3 6-12-2012
The Small Business Walk-through Energy Assessment Tool PROGRAM INSTRUCTIONS
This WTEA Tool is intended to be used for energy efficiency recommendations under the Small Business Program.
All projects MUST receive pre-approval before purchasing equipment or beginning work. Please review the program process and eligibility requirements on the program website as well as the Terms & Conditions on the application. Please contact the program office with any questions.
Program Process and Eligibility Requirements
Contact the Program Office |  |  | 866-353-5798
The Small Business Walkthrough Energy Assessment Report Generation Template
First, Enter Facility information on R1 Summary tab.
Second, Select measures on the "R2 Rec" tab. Be sure to include "No Cost/Low Cost" measures and check the "R2 NCLC" tab to reference measure descriptions.
Third, Enter ECM specific information:
If Lighting measures are recommended: Enter Lighting equipment in "W light exist" tab. Select lighting retrofits in "W light ECM select" tab. R2 lighting sheets (R2 T8T5, R2 CFL, R2 LED, R2 OtherLite) should populate automatically but check through them to make sure ECMs make sense. Sensors require additional input on "R2 OtherLite" tab.
If HVAC Measures are recommended: Enter HVAC information in "R2 HVAC Tune" or "R2 HVAC Repl" tabs as applicable. If HVAC sizing is unknown, enter HVAC equipment in "W HVAC" tab to estimate sizing information.
If Other Measures are recommended: Enter information on the applicable tabs (R2 Kitchen, R2 WaterHeat, R2 Vending, R2 Controls, R2 VFD, R2 Custom). Each individual measure tab has instructions as to what information is needed.
Fifth, Fill out R3 Facility Description
Sixth, Drag all unused measure tabs to the right of the R3 tab so they will not be printed.
Seventh, a) Review, revise, format for printing b) Submit for approval by designated reviewer c) Edit per reviewer feedback. d) Once approved, create PDF or paper copy to present to customer.
PepcoEnergyEfficiency@LMBPS.com
Measures recommended in this walk-through energy assessment are general recommendations and this report does not constitute pre-approval for installation of any equipment other than No Cost/Low Cost measures. All other measures that a customer decides to install still require a separate application form that details the specific equipment planned for installation.
Note - Please be sure to use the latest version of the application. Follow the link below to find the latest version
https://cienergyefficiency.pepco.com/Lighting.aspx
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
Printing Instructions for Page #
Select all of the report sheets to group them together. Select print and print report. It will be automatically numbered.
Be sure to ungroup sheets after printing.
If you use an insert in the report: place the dummy tab found at the back of the template in the location where the insert will be. One dummy tab per page of insert is required.
If you need to print only one page, in order for it to have the correct page #, you must group all pages of the report, select print, then select print pages and insert the page # you wish to print. Alternatively, you can open print review, select page set up, select custom footer, delete the &{page}, and manually enter the page #

## R Cover
S M A L L B U S I N E S S
Walk-Through Energy Assessment |  | No user entry on this page, other than pasting business image
for
Maryland
Survey Report Date:
Survey Prepared By:
Matrix Energy Services, Inc.
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
Insert Image of Business Here!!

## R TOC
Table of Contents
| 1. | Energy Survey Summary
| 2. | Recommendations |  |  | If there are no recommendations in one of the three "Recommendations" categories, delete that line.
|  | 2a. | Lighting
|  | 2b. | HVAC
|  | 2c. | Other
| 3. | Facility Description
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved

## R1 Sum
Energy Survey Summary | [6 empty] | Sect. 1
PEPCO provides energy surveys to help inform its customers about energy usage and energy costs.
The purpose of this survey is to evaluate your overall energy usage and energy consuming equipment to determine potential energy retrofit measures. With the implementation of the recommended energy measures you will lower your energy and operational costs, increase the asset value of your facility, increase employee productivity, and improve the comfort and appearance of your working environment. | [7 empty] | Fill in all customer contact information, building area and both building category and end use.
| Facility surveyed: |  |  |  | Survey #: | SWT-XXX-XXXX
| Facility Address: |  |  |  | Account #:
| Facility City: |  |  |  | Auditor: |  |  | Some energy calculations are based on building end use so it's important! Choose the closest option from the dropdowns if the specific type you want is unavailable. Choose the largest type by space for multi-use buildings.
| Facility State: | Maryland |  |  | Auditor Company: | Matrix Energy Services, Inc.
| Facility Zip Code: |  |  |  | Auditor Email:
| Contact: | Name |  |  | Auditor Phone:
|  | Phone Number |  |  | Date of Survey:
Building Area (sq.ft.):
Building Category:
| Assessment Overview |  |  |  | Building End Use:
| Equipment Category | Affects | Eligible for Incentives? | Comment |  |  |  | Use Pulldown Menus in table to address general state of all systems.
| Lighting* | Electric Bill |  | Upgrades shown on following pages
Air-Conditioning
Space Heating
Water Heating*
HVAC Controls
Refrigeration*
Cooking
Office/Computing*
Building Insulation
* Includes associated controls
PEPCO helps its customers by providing technical assistance and financial incentives for energy efficient investments. You may be eligible to receive a cash incentive if you implement the measures described in this survey.
Financial Summary
| Average Electric Cost Used |  | 0.15 | /kWh
| Potential Annual Cost Savings |  | 0
| Estimated Project Cost |  | 0
| Potential PEPCO Incentives |  | 0
| Net Installed Cost |  | 0
| Simple Payback |  |  | years
Recommendation Summary | Recommendation Summary
| Measure | Annual kWh Savings Potential | Annual Cost Savings Potential | Estimated Project Cost | PEPCO Small Business Incentive | Net Project Cost | Simple payback (yrs)
| Lighting | 0 | 0 | 0 | 0 | 0 | 0
| HVAC | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
Drop-down menu choices:
[10 empty] | Electric Bill | Yes | Condition appears to be satisfactory
[10 empty] | Fuel Bill | No | Consider replacement
[10 empty] | Both Bills |  | Upgrades shown on following pages
[10 empty] | Not applicable |  | Equipment inaccessible, condition unknown

## BusTypes (hidden)
Yes/No | Payment | Payment Name | Building Type | Project Type | Company Type | Company Status | How Heard | Lookup Range for Dropdown | BusinessTypeGeneral | Lookup Range for Dropdown
Yes | Customer (Account Holder) | CompanyName | Grocery | Failed/Degraded Equipment Replacement | Corporation | Large Business | Website |  | Agriculture | Choice_Agriculture
No | Contractor/Vendor | VendorName | Health | Early Equipment Replacement | LLC | Small Business: 8(a) certification | Approved Trade Ally |  | Industrial | Choice_Industrial
| Other (Specify): |  | Higher Education |  | Partnership | Small Business: Minority owned | Service Provider/Contractor |  | Large Commercial | Choice_LargeCommercial
|  |  | Industrial |  | Individual Partnership | Small Business: Woman owned | Program Representative (Identify -->): | Choice_Individual | Small Commercial | Choice_SmallCommercial
|  |  | Lodging |  | Not-for-Profit | Small Business: Veteran owned |  |  | Government | Choice_Government
|  |  | Multi-Family |  | Limited Partnership | Small Business: Other |  |  | Healthcare | Choice_Heathcare
Choose_Utility |  |  | Office |  | Trust |  |  |  | Education | Choice_Education
Pepco |  |  | Religious |  | S Corporation |  |  |  | Non-Profit | Choice_NonProfit
Delmarva Power |  |  | Restaurant | [5 empty] | Other
Retail
School
Warehouse
Other
BusinessTypeGeneral | Business Type Specific | Range Name |  | Put these in the DD | Standard list | SAVdee
Agriculture | Farms | Choice_Agriculture |  | Grocery Stores | Grocery | 139
| Dairies |  |  | Large grocery store chain | Grocery | 139
| Livestock farm |  |  | Convenience Stores | Grocery | 139
| Greenhouse |  |  | Hospitals | Health | 56
| Refrigerated Warehouse |  |  | Ambulatory health care | Health | 56
| Food Processor |  |  | Nursing or residential care | Health | 56
Industrial | Fabrication | Choice_Industrial |  | College or University | Higher Education | 171
| Process |  |  | Fabrication | Industrial | 23
| Heavy manufacturing |  |  | Process | Industrial | 23
| Warehouse |  |  | Heavy manufacturing | Industrial | 23
| Laboratories |  |  | Warehouse | Industrial | 23
| Biotech |  |  | Laboratories | Industrial | 23
Large Commercial | Office building | Choice_LargeCommercial |  | Biotech | Industrial | 23
| General retail |  |  | Farms | Industrial | 23
| Big box retail |  |  | Dairies | Industrial | 23
| Large grocery store chain |  |  | Livestock farm | Industrial | 23
| Warehouse |  |  | Greenhouse | Industrial | 23
| Convenience store |  |  | Refrigerated Warehouse | Industrial | 23
| Hospitality/Lodging |  |  | Food Processor | Industrial | 23
| Assisted Living |  |  | Data Center | Industrial | 23
| Data Center |  |  | Hospitality/Lodging | Lodging | 56
| Multifamily |  |  | Assisted Living | Lodging | 56
Small Commercial | Grocery Stores | Choice_SmallCommercial |  | Nursing or residential care | Lodging | 56
| Convenience store |  |  | Multifamily | Multi-Family | 56
| Restaurants |  |  | Office building | Office | 171
| Food Services |  |  | Small office | Office | 171
| Car dealerships |  |  | Large Non-Profit | Office | 171
| Small retail |  |  | Small Non-Profit | Office | 171
| Small office |  |  | Federal | Office | 171
| Multifamily |  |  | State | Office | 171
Government | Federal | Choice_Government |  | County | Office | 171
| State |  |  | Municipality | Office | 171
| County |  |  | Large Faith-Based | Religious | 6
| Municipality |  |  | Small Faith-Based | Religious | 6
Healthcare | Hospitals | Choice_HealthCare |  | Food Services | Restaurant | 36
| Ambulatory health care |  |  | Restaurants | Restaurant | 28
| Nursing or residential care |  |  | Big Box Retail | Retail | 171
Education | Schools | Choice_Education |  | General retail | Retail | 171
| College or University |  |  | Small Retail | Retail | 87
Non-Profit | Large Non-Profit | Choice_NonProfit |  | Car dealerships | Retail | 87
| Small Non-Profit |  |  | School | School | 39
| Large Faith-Based |  |  | Warehouse | Warehouse | 2
| Small Faith-Based |  |  | Other | Other | 56
Other

## R2 Rec
|  |  | Recommendations |  |  |  |  | Sect. 2
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
This section provides details on our energy saving recommendations for your facility. The first page provides a summary of our key findings and measure recommendations. The following pages provide detailed information on our measure recommendations.
Summary and Overview
Key Findings and Observations
Recommended Measures
Following listed items are the recommended measures that are eligible for Small Business Incentives. Detailed measure information can be found on the following pages. | [11 empty] | Recommended measures mix
1 | [10 empty] | Replace T12 lamps and magnetic ballasts with T8 lamps and electronic ballasts.
2 | [10 empty] | Replace T12/T8 lamps with higher efficiency T8 or T5 fixtures.
3 | [10 empty] | Replace T12/T8 lamps with LED fixtures
4 | [10 empty] | Replace incandescent and compact fluorescent lamps with LEDs.
5 | [10 empty] | Install new lighting fixtures with T8 lamps and electronic ballasts.
6 | [10 empty] | Replace HID light fixtures with new high bay fluorescent fixtures.
7 | [10 empty] | Replace standard HID lights with Pulse Start HID lights.
8 | [10 empty] | Install new energy efficient outdoor lighting.
9 | [10 empty] | Install occupancy sensors in your restrooms, equipment rooms, and storage rooms.
10 | [10 empty] | Install LED/LEC exit lights.
11 | [10 empty] | Optimize the performance of existing HVAC systems.
12 | [10 empty] | Replace HVAC units with new high efficiency HVAC units.
No-Cost/Low-Cost Measures | [10 empty] | Replace existing food service equipment with high efficiency food service equipment
The following measures are of no cost to you. If implemented, these measures will further assist your eligibility for higher cash incentives through the Small Business Program! Incentives shown (on the following pages) assume that you choose to implement these measures and take part in the Small Business Program. More information on these measures is covered on the following pages. | [10 empty] | Replace small, shaded-pole motors with ECM motors on refrigeration evaporator fans.
1 | [10 empty] | Install VFDs on motors over 2HP
2 | [10 empty] | Install evaporative fan controllers for walk-in coolers.
3 | [10 empty] | Install automated refrigerator door closers
4 | [10 empty] | Install vending machine controllers.
5 | [10 empty] | Install anti-sweat heater controls for glass refrigerated display doors.
6 | [10 empty] | Install new high efficiency or Energy Star water heaters
Other measures considered | [10 empty] | Install hotel room occupancy controls
The following measures were considered, but not evaluated for one or more of the following reasons: a) they are recommendations for future equipment purchases, b) there is insufficient information to fully analyze, or c) they are beyond the scope of this survey. | [10 empty] | Install office equipment controls
1
2 | [10 empty] | Other custom measure
3
[12 empty] | No-Cost Measures | Savings | Description
[11 empty] | Check and adjust thermostat's programmable settings |  | 10 | Programmable thermostats allow heat to be set back to a lower temperature and air conditioning to a higher temperature when the building is unoccupied, saving significant energy. Check to ensure that your settings match the building use and time of season. Recommended settings for saving energy while maintaining occupant comfort are to heat to 68˚F in the winter and cool to 74˚F in the summer. The rule of thumb is that you can save about 3% on your heating bill for every degree that you set back your thermostat.
[11 empty] | Activate energy-saving features of computers, monitors and copiers |  | 10 | Most current electronic equipment comes with software that shuts equipment down after a period of being left idle. However these settings are often overridden. Make sure that devices such as computers and monitors as well as photo copiers are configured to "sleep" or "standby" mode when left idle. This is a no-cost measure with immediate payback.
[11 empty] | Install reminder signs to turn off lights when not in use and in daylite areas |  | 10 | The walk-through of your facility revealed lights that were on where no workers or customers were present. A simple fix to this problem is to install stickers reminding employees to turn off the lights before they leave. A longer term fix that will save more energy is to install occupancy sensors.
[11 empty] | Check outdoor light controls for proper operation and settings |  | 10 | Outdoor lights are usually controlled by either timers or photo sensors. Adjust the timers according to the seasons and the length of daylight. Exterior lights on during the day are an indicator that either the timer or the sensor has failed. Photo sensors fail in the “On” position as a safety measure.
[11 empty] | Use window blinds to allow natural light to fill an area instead of artificial lights |  | 10 | Natural light is of course free, but it can be overpowering. Control the amount of light brought in with your blinds and shades. Adjust the blinds so the light is directed to the ceiling and allowed to diffuse back to the interior. This will eliminate glare and result in a more pleasant light level.
[11 empty] | Check and adjust water heater thermostat's settings to 115˚F - 120˚F range |  | 10 | Every water heater has a control to set the temperature. When the water heaters are installed they are often set around 130˚F or higher. For many small businesses hot water use limited to hand washing and general cleaning. The setting can be reduced to 115˚F - 120˚F. Every 10 degrees you dial down the thermostat can save 3 to 5 percent off your water heating costs. In food service environments check the local regulations for dishwasher cleaning. Where high temperatures are required, booster heaters can be installed at the work station .
Summary of Recommendations by Measure Type | [10 empty] | Make purchasing energy efficient equipment (Energy Star Qualified) standard practice |  | 10 | The Energy Star program covers a variety of products from computers, lighting, HVAC, water heaters, commercial food service equipment and appliances, and building products. Purchasing Energy Star qualified products ensures that you are selecting the most energy efficient products available. To see their list of qualified products go to: www.energystar.gov
Low Cost Measures
| Recommendation |  |  | kWh saved | Cost savings | Cost to retrofit | PEPCO Incentives | Net Cost | Simple payback (yrs) |  | Replace dirty air filters and clear blocked supply and return vents (HVAC and refrigeration) |  | 10 | Check your HVAC filters every 30 to 60 days and replace dirty filters. Heating and air conditioning systems depend on the free circulation of air to operate effectively. A blocked return or supply vent breaks this cycle and forces the HVAC system to work harder to maintain heating and cooling levels. An HVAC system with clogged filters or blocked vents is like driving uphill in a car with the brakes on and it can cause up to a 30% increase in energy costs. Limit: 3 filters per building.
NoCost/LowCost Measures |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Clean air filter and exposed/accessible condenser coils of A/C and refrigeration units |  | 10 | The condenser coils allow the heat from appliances to dissipate. Dust and dirt act as insulators on the coils preventing heat transfer. On stand up refrigerators, the coils run along the back. Other units may have vents along the floor in front of the refrigerator. Keep these areas clear of debris to keep your refrigerator cool. Use a broom or a vacuum to clean the coils.
Lighting | [10 empty] | Replace incandescent Lamps with CFLs |  | 147 | CFLs produce the equivalent amount of light for a fraction of the power and electric cost of a traditional incandescent lamp. CFLs also create much less heat – helping with your air conditioning costs. Even though CFLs are more expensive to purchase than incandescent lamps, they can save you up to 75% of your lighting costs. The savings in electrical costs will far exceed the initial purchase price. PEPCO offers cash incentives for replacing entire fixtures with CFL fixtures but for a limited number of screw-in bulbs we will pay the full amount.
| T5/T8 retrofits |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Replace incandescent Lamp with LED |  | 21 | LEDs produce the equivalent amount of light for a fraction of the power and electric cost of a traditional incandescent lamp. LEDs also create much less heat – helping with your air conditioning costs. Even though LEDs are more expensive to purchase than incandescent lamps, they can save you up to 90% of your lighting costs. The savings in electrical costs will far exceed the initial purchase price. PEPCO offers cash incentives for replacing entire fixtures with LED fixtures but for a limited number of screw-in bulbs we will pay the full amount. Limit: 1 per building.
| CFL retrofits |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Install timers on coffee makers and water coolers |  | 10 | Coffee makers and water coolers are devices that are often left on at night and on weekends when no employees are around to need them. Installing a simple programmed timer will reduce their use of energy to only when the building is occupied.
| LED retrofits |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Use "Smart Strips" for computer equipment and other multiple plug in loads |  | 24 | The smart strips are a convenient device that will allow you control multiple items on a single outlet strip. With the touch of one switch, you may turn on or off an entire group of computer equipment while other items are allowed to operate independently. Many electrical appliances continue to use energy even while they are turned off. Smart strips can keep these appliances from using energy while in the off mode. Another benefit is that many Smart Strips offer surge, Fax/Modem and Coaxial Cable protection. Depending on the application, Smart Strips can pay for themselves in approximately six weeks.
| Occupancy and Daylight sensors |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Add external insulation blanket to electric water heaters |  | 60 | Water heater wraps are available as kits. They are easy to install and the kits usually provide all material needed to complete the job. The wrap helps by reducing the heat loss from the tank. While you are at it, insulate the first six feet of exposed water pipes connected to the tank. Some newer models recommend that you should not wrap their product. Check your owner’s manual if in doubt. If there is no manual, place your hand on the tank. If you feel heat, then you will save by wrapping it. The savings can be as much as 25% of your water heating costs.
| High Intensity Discharge retrofits |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Insulate exposed water heater pipes |  | 150 | While modern water heaters come with internal tank insulation, bare copper pipes emerging from the top can siphon heat out into the room. If the water heater is in conditioned space, the energy loss is double because the air conditioning needs to remove this heat! Pipe insulation is cheap and easy to install yourself. Make sure to insulate hot water pipes on any portion you can access as well as 1-1.5' on the cold water inlet side.
HVAC | [10 empty] | Replace worn gaskets on exterior doors |  | 10 | • Leaking gaskets make it hard for your building to hold temperature, resulting in compressor overloads. • Cracked gaskets pose a health hazard by providing an ideal, hard-to-clean breeding ground for salmonella and other disease causing microorganisms. • Escaping cold air causes your electric meter to spin even faster. • Limit: 20 feet of gasket material.
| Maintenance and repair |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | Replace worn gaskets on refrigerator doors |  | 10 | • Leaking gaskets make it hard for your cooler to hold temperature, resulting in compressor overloads. • Cracked gaskets pose a health hazard by providing an ideal, hard-to-clean breeding ground for salmonella and other disease causing microorganisms. • Escaping cold air causes your electric meter to spin even faster. • Limit: 20 feet of gasket material.
| HVAC unit replacement |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Install insulation gaskets on switch and outlet plates on exterior walls |  | 10 | Insulation gaskets on switch and outlet plates are very inexpensive and easy to install. They fill gaps where the wall insulation was cut out to install the switch or plug. Place your hand over the plate or blow out a match to see if the smoke moves. It may be surprising how much air flows through these areas.
| Hotel HVAC Controls |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Reduce air infiltration using caulk and spray foam (apply latter to increase insulation) |  | 10 | Weather-strip around windows and doors to eliminate drafts. Use caulk to seal cracks and penetrations around windows, doors and other penetrations on exterior walls. Spray foam products work well to seal large irregular shaped openings where plumbing or electrical wires penetrate the walls. Weather sealing products are inexpensive and they can save you up to 4 percent of your heating and cooling costs.
Other
| Refrigeration Equipment |  |  | 0 | 0 | 0 | 0 | 0
| Kitchen Equipment |  |  | 0 | 0 | 0 | 0 | 0
| Variable Frequency Drives |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Promote participation in the SB DLC Program - includes a free Programmable thermostat |  | 10 | The PEPCO Small Business Direct Load Control programs provides customers with a programmable thermostat which can be controlled by the utility in times of high electricity demand. The energy and financial savings are high in exchange for allowing cooling set points to be raised just a couple of degrees a few times per year.
| Water Heater Replacement |  |  | 0 | 0 | 0 | 0 | 0
| Vending Machine Controls |  |  | 0 | 0 | 0 | 0 | 0
| Office Controls |  |  | 0 | 0 | 0 | 0 | 0
| Custom and Alternative Measures |  |  | 0 | 0 | 0 | 0 | 0 |  |  | Other Measures Considered List
|  |  |  | 0 | 0 | 0 | 0 | 0
Install lighting control systems.
Optimize lighting by commissioning your lighting controls.
Replace HVAC units with new high efficiency HVAC units.
Perform a test and balance on the HVAC air supply system(s).
Energy savings and cost estimates | [10 empty] | Optimize HVAC systems by commissioning the building automation system controls.
| This report was prepared using proprietary software developed by Lockheed Martin Energy Services. The potential energy savings shown in this report have been calculated based upon an average energy cost of $0.15/kWh, standard energy engineering practices, and the author's practical experience. Actual results may vary due to a variety of reasons, such as facility usage changes, occupancy changes, weather variations, operational changes, and others. | [9 empty] | Eliminate unnecessary HVAC run time during unoccupied hours.
| The cost to install energy saving measures can be obtained from a variety of sources. Our cost estimates are based on turnkey installations by professional contractors. They are based on typical retrofit costs that may or may not include all of the specifics associated with your particular facility. | [9 empty] | Replace selected motors with new high efficiency motors.
Optimize compressed air systems.
Have pump, blower, and exhaust fan systems checked for operational efficiency.
Replace existing single pane windows with double pane windows.
Test and optimize boiler operation.
Install Cool Roof products when reroofing is required.
Install heat recovery systems.
Install energy efficient hot water heaters.
Install low-e window film
PEPCO Small Business Program
PEPCO offers enhanced cash incentives to qualifying small businesses within our Maryland territory. By participating in this walk-through assessment you're already well on your way to qualifying!
Next steps: (1) Complete the No-Cost/Low-Cost measures (2) Determine which measures to complete (3) Work with a Program approved Trade Ally to submit a project application for pre-approval (4) Contact the Program office if you have questions. 1-866-353-5798
Email: PepcoEnergyEfficiency@LMBPS.com, Web: https://cienergyefficiency.pepco.com/SmallBus.aspx
Highlight the most important discoveries or any findings that address customer specific issues, such as a high bill complaint. If none, type "N/A"
Note: You can select standard descriptions from dropdown menus or you can add to, or type your own description. For long descriptions, simply increase the row's height by dragging the cursor at the bottom of the row number.
If you have more than 7 recommended measures there are additional lines that can be unhidden. If you do this check to make sure pages still format nicely for printing!
Save Time and Money. Act now!
For measures that are not recommended, hide the relevant line on the printed report. The values on these lines should be zero.

## R2 NCLC
No-Cost/Low-Cost Measures | Sect. 2
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
The following measures, if implemented, will allow you to be eligible for the enhanced incentives available through the Small Business Program. These measures should be easy to implement through in-house labor or with the assistance of a trade ally.
Recommendations and descriptions should fill based on entry on the previous "R2 Rec" page. Use the last space at the bottom to write in any additional measures you want to recommend.
Other Measures (Write in any opportunities identified not listed above)
There are many ways to reduce energy costs and consumption. The list above provides for some of the most common Low/No Cost opportunities. Use this space to list any other measures identified during the walk through.

## R2 T8T5
| Lighting Opportunities | [6 empty] | Sect. 2a
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
Report table will autofill. Hide unused lines. If you have more than one page of recommendations (more than 7 areas and light types) unhide lines between 38 and 83)
Retrofit Description
T12 lamps with magnetic ballasts are obsolete by today's standards. T8 lamps driven by electronic ballasts are not only more energy efficient but they last longer and produce a higher quality of light. For some applications, the newer T5 lamps can be an even greater improvement, though they are not suitable to all applications due to their intense concentrated light. | [9 empty] | FALSE | [7 empty] | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure. Cost entered should be TOTAL cost for the measure.
Lighting technology is changing fast. New generations of more efficient T8 lamps and electronic ballasts are continually introduced into the market. In general, purchase the most advanced generation of lamps available. The most advanced lamps allow for more aggressive delamping (e.g., replacing four lamps with two lamps) that maximizes your energy savings.
Savings Analysis
Retrofit description |  | Area | Qty | Energy savings (kWh) | Demand reduction (kW) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive |  | Retrofit description |  | Qty | Energy savings (kWh) | Demand reduction (kW) | Energy cost savings | Cost to retrofit | Incentive
1. | [8 empty] | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
2. | [8 empty] | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
3. | [8 empty] | 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
4. | [8 empty] | 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
5. | [8 empty] | 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
6. | [8 empty] | 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
7. | [8 empty] | 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
8. | [8 empty] | 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
9. | [8 empty] | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
10. | [8 empty] | 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
11. | [8 empty] | 11 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
12. | [8 empty] | 12 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
13. | [8 empty] | 13 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
14. | [8 empty] | 14 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
15. | [8 empty] | 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
16. | [8 empty] | 16 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
17. | [8 empty] | 17 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
18. | [8 empty] | 18 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
| Totals: |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
T8 and T5 Lamps and Fixtures
Trade Ally Cost Override?

## R2 LED
| Lighting Opportunities | [6 empty] | Sect. 2a
Copyright © 2012 Potomac Electric Power Company
[8 empty] | All Rights Reserved | [9 empty] | Report table will autofill. Hide unused lines. If you have more than one page of recommendations (more than 7 areas and light types) unhide lines between 39 and 80)
Retrofit Description
While LEDs are in many ways an emerging lighting technology, for certain applications they are already a practical solution. The initial cost is high but the lamp life is very long, from 20,000 to 100,000 hours. | [9 empty] | FALSE | [7 empty] | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure. Cost entered should be TOTAL cost for the measure.
Lighting technology is changing fast. New generations of more efficient LEDs are continually introduced into the market. In general, purchase the most advanced generation of lamps available.
Exit Signs that utilize LED lights use 73% less energy than traditional exit signs with incandescent lights. Additionally, a new technology is available that promises even more energy and maintenance savings. A light emitting capacitor panel (LEC) uses only 0.35 watts and lasts up to 30 years.
LED Retrofit Opportunities
Retrofit description |  | Area | Qty | Energy savings (kWh) | Demand reduction (kW) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive |  | Retrofit Description |  | Qty | Energy savings (kwh) | Demand Reduction (kW) | Energy Cost Savings | Cost to Retrofit | Incentive
1. | [8 empty] | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
2. | [8 empty] | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
3. | [8 empty] | 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
4. | [8 empty] | 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
5. | [8 empty] | 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
6. | [8 empty] | 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
7. | [8 empty] | 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
8. | [8 empty] | 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
9. | [8 empty] | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
10. | [8 empty] | 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
11. | [8 empty] | 11 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
12. | [8 empty] | 12 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
13. | [8 empty] | 13 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
14. | [8 empty] | 14 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
15. | [8 empty] | 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
16. | [8 empty] | 16 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
17. | [8 empty] | 17 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
Existing: |  | 0 | [7 empty] | Existing Fixture: | 0
Proposed retrofit: |  | 0 | [7 empty] | Replacement Fixture: | 0
| Totals: |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Light Emitting Diodes (LEDs)
Trade Ally Cost Override?

## R2 CFL
| Lighting Opportunities | [6 empty] | Sect. 2a
[8 empty] | Copyright © 2012 Potomac Electric Power Company | [9 empty] | Report table will autofill. Hide unused lines.
[8 empty] | All Rights Reserved | [9 empty] | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure. Cost entered should be TOTAL cost for the measure.
Retrofit Description
Compact Fluorescent Lamps (CFLs) are replacing incandescent lamps for most general lighting applications. CFLs use 67% less energy than an incandescent and last more than 10 times longer. Recent improvements in CFL technology have greatly improved the quality of light and minimized warm up time (time it takes for the lamp to reach full brightness). Typical applications include canned recessed downlights, sconces, table lamps, task lights, closets, and wall washers.
Recommendation: Replace the following incandescent lamps with CFL fixtures. To ensure satisfactory light levels, replace the incandescent lamp with a CFL rated at approximately one third (33%) of the incandescent lamp wattage. For example, a 25w CFL will provide slightly more light and is a suitable replacement for a 75w incandescent. | [9 empty] | FALSE
Savings Analysis
Retrofit description |  | Area | Qty | Energy savings (kWh) | Demand reduction (kW) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive |  | Proposed Retrofit |  | Qty | Energy savings (kwh) | Demand Reduction (kW) | Energy Cost Savings | Cost to Retrofit | Incentive
1. | [8 empty] | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
| Existing: | 0 | [7 empty] | Existing Fixture: | 0
| Proposed retrofit: | 0 | [7 empty] | Replacement Fixture: | 0
2. | [8 empty] | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
| Existing: | 0 | [7 empty] | Existing Fixture: | 0
| Proposed retrofit: | 0 | [7 empty] | Replacement Fixture: | 0
3. | [8 empty] | 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
| Existing: | 0 | [7 empty] | Existing Fixture: | 0
| Proposed retrofit: | 0 | [7 empty] | Replacement Fixture: | 0
4. | [8 empty] | 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
| Existing: | 0 | [7 empty] | Existing Fixture: | 0
| Proposed retrofit: | 0 | [7 empty] | Replacement Fixture: | 0
5. | [8 empty] | 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
| Existing: | 0 | [7 empty] | Existing Fixture: | 0
| Proposed retrofit: | 0 | [7 empty] | Replacement Fixture: | 0
6. | [8 empty] | 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
| Existing: | 0 | [7 empty] | Existing Fixture: | 0
| Proposed retrofit: | 0 | [7 empty] | Replacement Fixture: | 0
7. | [8 empty] | 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Location: | 0
| Existing: | 0 | [7 empty] | Existing Fixture: | 0
| Proposed retrofit: | 0 | [7 empty] | Replacement Fixture: | 0
| Totals: |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Compact Fluorescent Fixtures
Trade Ally Cost Override?

## R2 OtherLite
| Lighting Opportunities | [5 empty] | Sect. 2a
[8 empty] | Copyright © 2012 Potomac Electric Power Company | [7 empty] | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure. (Indicated by *). Cost entered should be TOTAL cost for the measure.
[8 empty] | All Rights Reserved | [15 empty] | Report table will autofill. Hide unused lines. If you have more than 4 areas and light types unhide lines between 13 and 25.
Occupancy and Daylighting Sensors
Occupancy sensors are best suited for rooms with highly variable and unpredictable occupancy patterns. Sensor selection, positioning, and testing is essential to ensure successful operation of the sensor as well as occupant acceptance of the control. Passive Infrared (PIR) sensors must "see" heat and are best used for a small room as their range limit is typically 15'. Ultrasonic sensors emit ultrasonic waves to detect motion and are better suited for larger rooms. However, ultrasonic sensors are more susceptible to "false" triggering. Dual technology sensors combine both PIR and ultrasonic technologies to provide optimum performance. It is essential that the sensor be commissioned, or fully tested in place to ensure sensor operation is correct, time delay settings are optimized, and false triggering is minimized or eliminated. Once in place, occupants and maintenance personnel should be trained in the operation and upkeep of the sensor. Daylight sensors turn lighting off when available sunlight is sufficient to illuminate a space. They are recommended for exterior lighting, atrium lighting, and perimeter lighting near windows. They are an alternative to timers that allows flexibility for lighting to turn on at different times as the seasons and weather change. | [15 empty] | Table should autopopulate with fixtures you recommended sensors for in the "W light ECM Select" tab. If a replacement for those fixtures is selected, the replacement will show. Select room type, sensor type and number of sensors below. Reference table at right to make sure sensor requirements are met. If you have more than 4 areas and light types unhide lines between 11 and 18. | [6 empty] | Sensor Code | Sensor Type | Limitations. Check system kW at left to make sure wattage criteria are met!
Recommendation: | Install occupancy sensors or daylighting control sensors in the following areas | [8 empty] | FALSE
Area served | Lighting to be controlled |  | Sensor Qty | Fixture Qty | Energy savings (kWh) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive |  |  | Total Rebate | Per sensor | payback after rebate | Op hrs schedule | Op hrs | Room Type | Control Savings | System kW | kWh savings | cost to retrofit | Sensor type (see chart at right) | Sensor Quantity | LTC1 | Occupancy Control - Wall Mount (near or replacing wall switch) | Minimum of 0.05kW controlled per sensor.
[5 empty] | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | LTC2 | Occupancy Control – Fixture Mounted | Minimum of 0.04kW controlled per sensor.
[5 empty] | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | LTC3 | Occupancy Control - Remote or Ceiling Mounted | Minimum of 0.120 kW controlled per sensor.
[5 empty] | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | LTC4 | Occupancy Control – with Step-Dimming Capability | Minimum of 0.175 kW controlled per sensor.
[5 empty] | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | LTC5 | Daylight Control – Off / On | Each sensor must control at least four HPT8, RWT8, or T5/T5HO ballasts; or four CFL fixtures.
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 7 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 8 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 11 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 14 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
|  |  | 0 |  | 0 | 0 | 0 | 0 |  | 15 | 0 | 0 | #DIV/0! |  | 0 |  | 0% | 0 | 0 | 0 |  | 0
Total |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | #DIV/0! | [9 empty] | LTC6 | Daylight Controls – Continuous or Step-Dimming Capability
[23 empty] | Fixture Code | Lighting Controls | Incentive
[16 empty] | Room type | OC savings | Install $ | Sensor | Labor
[16 empty] | Private office | 40% | 125 | 65 | 60 |  |  | LTC1 | Occupancy Controls - Wall Mount (near or replacing wall switch) | 60 | /Sensor
[16 empty] | Conference room | 55% | 240 | 120 | 120 |  |  | LTC2 | Occupancy Controls – Fixture Mounted | 80 | /Sensor
[16 empty] | Corridor | 60% | 125 | 65 | 60 |  |  | LTC3 | Occupancy Controls - Remote / Ceiling Mounted | 160 | /Sensor
[16 empty] | copier room | 25% | 105 | 45 | 60 |  |  | LTC4 | Occupancy Controls – with Step-Dimming Capability | 120 | /Ballast
[16 empty] | break room | 45% | 105 | 45 | 60 |  |  | LTC5 | Daylight Controls – Off / On | 45 | /Sensor
[16 empty] | general | 25% | 180 | 90 | 90 |  |  | LTC6 | Daylight Controls – with Continuous or Step-Dimming Capability | 130 | /Ballast
[16 empty] | exterior | 50%
[16 empty] | storage room | 5% | 105 | 45 | 60 |  |  | LTC7 | Occupancy Controls - Wall Mount (near or replacing wall switch) | 25 | /Door
Source: SB Measure List, updated 05/14/12 (CRA)
HID Retrofits | [13 empty] | Note: If selecting LTC7, enter number of doors in "Sensor Quantity" box | [8 empty] | LTC7 | Occupancy Control for LED Fixtures located within a refrigerated case (can only be used with measure LTL16)
High Intensity Discharge, or HID, fixtures are commonly used in areas with high ceilings, such as warehouse space, parking garages, gas stations, or pole lighting.Typical HID fixtures include Metal Halide, High Pressure Sodium, and, to a lesser degree, Mercury Vapor fixtures. There are a number of energy efficiency options for HID fixtures. Upgrading to Pulse-Start Metal Halide, High Bay T5/T8, or LED Fixtures are some of the options availble.
Recommendation: | Retrofit the following fixtures with Pulse Start Metal Halide fixtures | [7 empty] | Report table will autofill. Hide unused lines. If you have more than 4 areas and light types unhide lines between 52 and 60.
Existing fixture |  | Retrofit fixture |  | Qty | Energy savings (kWh) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive | [19 empty] | Proposed Retrofit | Qty | Energy savings (kwh) | Demand Reduction (kW) | Energy Cost Savings | Cost to Retrofit | Incentive
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [9 empty] | If you overrode costs above you must enter cost information in this section as well. Enter on EVERY line with a measure. | [8 empty] | 1 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 2 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 3 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 4 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 5 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 6 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 7 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 8 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 9 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 10 |  | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0 | 0 | 0 | [18 empty] | 11 |  | 0 | 0 | 0 | 0 | 0 | 0
Total |  |  |  | 0 | 0 | 0 | 0 | 0 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0
DESCRIPTIONS
Sensor & HID Retrofits
Trade Ally Cost Override?

## R2 HVAC Tune
|  | HVAC Opportunities | [5 empty] | Sect. 2b
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
Optimize the operating performance of your current HVAC system(s)
Air conditioning (AC) units that run at their optimum performance levels save energy and money. Industry studies have indicated that 8 out of 10 units are under-performing and that savings of up to 35% can be achieved through an AC unit tune up. Common unit deficiencies that are addressed in a tune up are dirty condenser coils, low refrigerant charge, low airflow, and economizer failure. In addition to saving energy, a tune up will improve the reliability and longevity of your AC equipment. It also ensures that you can depend upon your air conditioning to work when its most needed. | [10 empty] | Enter location, select measure type from pulldown, enter number and size of HVAC. Report table will autofill. Hide unused lines.
Minimize air conditioning duct leakage
Recent studies have shown that it is not uncommon for existing air distribution systems in commercial buildings to have air leakage rates higher than 30%. Pressurization testing and leakage repair can minimize, or completely eliminate, these losses.
Recommendation: If you are experiencing heating and cooling problems or suspect your ductwork is leaking, have a professional service contractor inspect and perform a duct leakage test. Replace all cloth-backed duct tape with mastic, tape, aerosol sealant, or other devise that meets UL181, UL181A, UL181B standards. If duct insulation is in need of replacement, upgrade to R-8 insulation.
Recommendation: Hire a professional service contractor to perform annual preventative maintenance. Initial preventative maintenance will include system diagnostics to identify typical system deficiencies, as listed above. Correcting system deficiencies ensures that your HVAC system(s) will operate efficiently. | [9 empty] | Line Item | No Vendor Cost Override is given because 100% of reasonable costs will be covered for Small Business customers |  |  |  |  | Number of Compressors | Pretest results indicate SEE >95% OR unable to achieve SEE >90% in post-testing | Testing Incentive | Per Unit Incentive | Total Incentive | Projected Energy Savings | Projected Cost | HVAC unit site designation and/or location (attach additional sheets as necessary) | Unit age (year of manufacture, estimate if necessary) | Occupied hours per day for space served by this unit | Typical number of occupants in area served | Economizer appears operational (Y, N or ?) | Economizer control type (DB, Ent, Dual Ent) | Indoor CO2 ppm and economizer in use (Y or N) | Refrigerant type | Date of last maintenance | Is condenser coil ground‐mounted & within 5 feet of grass or other vegetation? | Is condenser coil roof‐mounted & within 30 feet of vegetation or a pollen source? | Is condenser coil roof mounted & within 30 feet of kitchen or other grease laden exhaust? | Is condenser coil roof mounted & within 30 feet of dryer or other particle laden exhaust? | Has the HVAC unit’s previous chemical coil cleaning & power washing been more than 3 years? | Is there evidence of material trapped between the condenser coil fins in 20%–40% of the coil area? | Is the HVAC unit a split system?
Savings analysis | [12 empty] | $ -
The following HVAC units were selected for their efficiency improvement potential. See the analysis reports in Appendix II for more detail and evaluation criteria. The recommended maximum repair budget is based upon a simple payback of three years.
Unit # | HVAC Location Served | Measure Type | Tons Per Unit | Qty | Energy savings (kWh) | Electric cost savings | Measure Cost | PEPCO Incentive | Net Cost | Totals | Location of HVAC (Floor/Room) | Measure Type |  | Number of Units | Tonnage per Unit | 18 |  | 0 | 675 | 0 | 0 | 0
1 |  |  | 0 |  | 0 | 0 | 0 | 0 | $ - | 1 |  | Enhanced Tune-up |  | 0 | 0 | 1 | No | 0 | 175 | 0 | 0
2 | [6 empty] | 0 | 0 | $ - | 2 |  | Economizer Testing |  | 0 |  | 2 | No |  | 50 | 0
3 |  |  | 0 |  | 0 | 0 | 0 | 0 | $ - | 3 |  | Enhanced Tune-up |  | 0 | 0 | 1 | No |  | 175 | 0 | 0
4 | [6 empty] | 0 | 0 | $ - | 4 |  | Economizer Testing |  | 0 |  | 2 | No |  | 50 | 0
5 |  |  | 0 |  | 0 | 0 | 0 | 0 | $ - | 5 |  | Enhanced Tune-up |  | 0 | 0 | 1 | No |  | 175 | 0 | 0
6 | [6 empty] | 0 | 0 | $ - | 6 |  | Economizer Testing |  | 0 |  | 2 | No |  | 50 | 0
7 | 0 |  | 0 | 0 | [5 empty] | 7 | [5 empty] | 1 | No
8 | 0 |  | 0 | 0 | [5 empty] | 8 | [5 empty] | 1 | No
9 | 0 |  | 0 | 0 | [5 empty] | 9 | [5 empty] | 1 | No
10 | 0 |  | 0 | 0 | [5 empty] | 10 | [5 empty] | 1 | No
11 | 0 |  | 0 | 0 | [5 empty] | 11 | [5 empty] | 1 | No
12 | 0 |  | 0 | 0 | [5 empty] | 12 | [5 empty] | 1 | No
13 | 0 |  | 0 | 0 | [5 empty] | 13 | [5 empty] | 1 | No
14 | 0 |  | 0 | 0 | [5 empty] | 14 | [5 empty] | 1 | No
15 | 0 |  | 0 | 0 | [5 empty] | 15 | [5 empty] | 1 | No
| Total |  | 0 | 0 | 0 | 0 | 0 | 0 | $ -
Choose_YesNo?
Please note that if your HVAC unit is older than 17 years, it is past it's recommended useful life. Reliability issues and maintenance costs on these older units increase dramatically. If you consider the increasing maintenance costs, emergency repair costs, PEPCO equipment incentives, and the greater than 50% energy cost savings associated with new equipment, the most cost effective action to take is to install a new high efficiency HVAC unit. | [37 empty] | Yes
No
Unknown
Choose_Economizer
DB
Enthalpy
Dual-Enthalpy
Choose_Measure
[38 empty] | Enhanced Tune-up | (see below)
[38 empty] | Economizer Testing | 50
[38 empty] | Economizer Repair | 150
[38 empty] | Dual-Enthalpy Economizer Upgrade | 150
[38 empty] | Ventilation Air Quantity Optimization | 150
[38 empty] | Demand-Controlled Ventilation | 200
[38 empty] | Enhanced Tune-up: Single Compressor | 175
[38 empty] | Enhanced Tune-up: Multiple Compressors | 250
[38 empty] | Enhanced Tune-up: Pretest results indicate SEE >95% or unable to achieve SEE >90% in post-testing | 35
3-1
Maintenance & Repair

## R2 Kitchen
Refrigeration and Kitchen Equipment |  |  |  |  | Sect. 2c
[6 empty] | Copyright © 2012 Potomac Electric Power Company | [8 empty] | Measure Code | Refrigeration Equipment | Size Criteria | Incentive per Unit |  | EUL (Years) | SBC Incentive |  | Energy Savings Per Unit | Installation Cost Per Unit | Assumptions
All Rights Reserved
[7 empty] | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure. (Indicated by *). Cost entered should be TOTAL cost for the measure. |  |  |  | FALSE | [7 empty] | Unit |  | Incentive | Unit
Refrigeration Equipment | [14 empty] | RF01 | Anti-Sweat Heat Control for Cooler Doors | na | 40 | Door | 10 | 80 | /Door | 386 | 100 | 4 doors per controller
Refrigeration uses large amounts of electric energy at many businesses, such as grocery stores, restaurants, food and industrial processors, hospitals, and lodging establishments. If your business has refrigeration, installing energy efficient equipment and controls on existing or new equipment can help you reduce energy costs, enhance equipment reliability, and improve your bottom line. | [6 empty] | REFRIGERATION CALCULATIONS - Enter Existing Equip, Proposed Equip, and Quantity Here. Report page will autofill. Hide unused lines. | [7 empty] | RF02 | Anti-Sweat Heat Control for Freezer Doors | na | 40 | Door | 10 | 80 | /Door | 404 | 100 | 4 doors per controller
[15 empty] | RF03 | Reach-In Door Closer for Cooler - Glass Door | na | 40 | Door | 10 | 80 | /Door | 373 | 100 | glass door
Existing Equipment | Qty | Recommended Retrofit or Replacement | Energy savings (kWh) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive | Exisiting Equipment | Proposed Equipment/Measure | Qty | Energy Savings kWh | Energy Cost $ Savings | Cost to Retrofit | Incentive |  | RF03 | Reach-In Door Closer for Cooler - Solid Door | na | 40 | Door | 10 | 80 | /Door | 373 | 100 | solid door | Proposed Equip-Generated from Matrix
[11 empty] | 0 | 0 | 0 |  | RF04 | Reach-In Door Closer for Freezer - Glass Door | na | 50 | Door | 10 | 80 | /Door | 560 | 100 | glass door
[11 empty] | 0 | 0 | 0 |  | RF04 | Reach-In Door Closer for Freezer - Solid Door | na | 50 | Door | 10 | 80 | /Door | 560 | 100 | solid door
[11 empty] | 0 | 0 | 0 |  | RF05 | Strip Curtains for Walk-In Coolers (per ft^2) | na | 3 | ft^2 | 5 | 10 | ft^2 | 111.3333 | 12.5 | 1 ft^2
[11 empty] | 0 | 0 | 0 |  | RF06 | Strip Curtains for Walk-In Freezers (per ft^2) | na | 3 | ft^2 | 5 | 10 | ft^2 | 295.125 | 12.5 | 1 ft^2
[11 empty] | 0 | 0 | 0 |  | RF07 | Strip Curtains for Walk-In Freezers (per ft^2) | na | 4 | ft^3 | 5 | 10 | ft^3 | 295.125 | 12.5 | 2 ft^2
[11 empty] | 0 | 0 | 0 |  | RF06 | Strip Curtains for Walk-In Freezers (per ft^2) | na | 3 | ft^2 | 5 | 10 | ft^2 | 295.125 | 12.5 | 1 ft^2
[11 empty] | 0 | 0 | 0 |  | RF06 | Strip Curtains for Walk-In Freezers (per ft^2) | na | 3 | ft^2 | 5 | 10 | ft^2 | 295.125 | 12.5 | 1 ft^2
Total | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | RF08 | ECM Evaporative Fan Motor for Walk-In Freezer | na | 50 | Motor | 15 | 100 | /Motor | 571.8 | 125
[7 empty] | If you overrode costs above you must enter cost information in this section as well. (Indicated by *) | [7 empty] | RF09 | ECM Evaporative Fan Motor for Display Cooler | na | 50 | Motor | 15 | 100 | /Motor | 336.9 | 125
Commercial Kitchen Equipment | [14 empty] | RF10 | ECM Evaporative Fan Motor for Display Freezer | na | 50 | Motor | 15 | 100 | /Motor | 431.7 | 125
Food preparation and storage equipment uses a large portion of the energy in grocery stores, restaurants, convenience stores and cafeterias. If your business has a commercial kitchen, the C&I Energy Savings Program can help you save energy and money. In addition to lowering energy costs, efficiency improvements can enhance the performance of your restaurant, cafeteria, or kitchen for your guests and staff. We offer cash incentives for upgrading to new energy efficient ENERGY STAR® qualified electric equipment for food preparation. | [6 empty] | KITCHEN EQUIPMENT CALCULATIONS - Enter Existing Equip and Quantity Here. There is only one retrofit type available for each type of equipment. Report page will autofill. Hide unused lines. | [7 empty] | RF11 | Evaporator Fan Controller on Existing Shaded-Pole Meter | na | 75 | Motor | 10 | 150 | /Motor | 333.3333 | 187.5
[15 empty] | RF12 | Solid Door Reach-In Refrigerators <19ft^3 | < 19 cubic ft | 75 | Equipment Item | 12 | 1000 | /Equipment Item | 445 | 2000
Existing Equipment | Qty | Recommended Replacement | Energy savings (kWh) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive | Existing (enter from dropdown) | Replacement (will autofill) | Qty (enter) | Energy Savings kWh | Energy Cost $ Savings | Cost to Retrofit | Incentive |  | RF13 | Solid Door Reach-In Refrigerators 19-20ft^3 | 19-20 cubic ft | 100 | Equipment Item | 12 | 1350 | /Equipment Item | 650 | 2700
[11 empty] | 0 | 0 | 0 |  | RF14 | Solid Door Reach-In Refrigerators 21-60ft^3 | 21-60 cubic ft | 150 | Equipment Item | 12 | 2000 | /Equipment Item | 942 | 4000
[11 empty] | 0 | 0 | 0 |  | RF15 | Solid Door Reach-In Refrigerators 61-90ft^3 | 61-90 cubic ft | 225 | Equipment Item | 12 | 3000 | /Equipment Item | 1351 | 6000
[11 empty] | 0 | 0 | 0 |  | RF16 | Solid Door Reach-In Freezers <19ft^3 | < 19 cubic ft | 100 | Equipment Item | 9 | 1300 | /Equipment Item | 588 | 2600
[11 empty] | 0 | 0 | 0 |  | RF17 | Solid Door Reach-In Freezers 19-20ft^3 | 19-20 cubic ft | 200 | Equipment Item | 9 | 2000 | /Equipment Item | 1209 | 4000
[11 empty] | 0 | 0 | 0 |  | RF18 | Solid Door Reach-In Freezers 21-60ft^3 | 21-60 cubic ft | 320 | Equipment Item | 9 | 3000 | /Equipment Item | 2077 | 6000
[11 empty] | 0 | 0 | 0 |  | RF19 | Solid Door Reach-In Freezers 60-91ft^3 | 61-90 cubic ft | 500 | Equipment Item | 9 | 4000 | /Equipment Item | 3303 | 8000
Total | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | RF20 | Glass Door reach-In Refrigerators <19ft^3 | < 19 cubic ft | 75 | Equipment Item | 12 | 1000 | /Equipment Item | 471 | 2000
[15 empty] | RF21 | Glass Door reach-In Refrigerators 19-20ft^3 | 19-20 cubic ft | 100 | Equipment Item | 12 | 1350 | /Equipment Item | 645 | 2700
[15 empty] | RF22 | Glass Door reach-In Refrigerators 21-60ft^3 | 21-60 cubic ft | 125 | Equipment Item | 12 | 2000 | /Equipment Item | 893 | 4000
[15 empty] | RF23 | Glass Door reach-In Refrigerators 61-90ft^3 | 61-90 cubic ft | 150 | Equipment Item | 12 | 3000 | /Equipment Item | 1240 | 6000
[15 empty] | RF24 | Ice Machine - CEE Tier 1 small | <450 lbs per 24 hrs | 50 | Equipment Item | 8 | 700 | /Equipment Item | 472.4 | 1400
[15 empty] | RF25 | Ice Machine - CEE Tier 1 med | 451-1000 lbs per 24 hrs | 100 | Equipment Item | 8 | 1500 | /Equipment Item | 1010.4 | 3000
[15 empty] | RF26 | Ice Machine - CEE Tier 1 large | >1000 lbs per 24 hrs | 150 | Equipment Item | 8 | 2000 | /Equipment Item | 1511.2 | 4000
[15 empty] | RF27 | Ice Machine - CEE Tier 2 Cube & Nugget small | <450 lbs per 24 hrs | 75 | Equipment Item | 8 | 800 | /Equipment Item | 590.5 | 1600
[15 empty] | RF28 | Ice Machine - CEE Tier 2 Cube & Nugget med | 451-1000 lbs per 24 hrs | 125 | Equipment Item | 8 | 1600 | /Equipment Item | 1263 | 3200
[15 empty] | RF29 | Ice Machine - CEE Tier 2 Cube & Nugget large | >1000 lbs per 24 hrs | 150 | Equipment Item | 8 | 2200 | /Equipment Item | 1889 | 4400
[15 empty] | RF30 | Ice Machine - CEE Tier 2 Flake small | <450 lbs per 24 hrs | 100 | Equipment Item | 8 | 1000 | /Equipment Item | 590.5 | 2000 |  | KITCHEN EQUIPMENT CALCULATIONS
[15 empty] | RF31 | Ice Machine - CEE Tier 2 Flake med | 451-1000 lbs per 24 hrs | 175 | Equipment Item | 8 | 1800 | /Equipment Item | 1263 | 3600
[15 empty] | RF32 | Ice Machine - CEE Tier 2 Flake large | >1000 lbs per 24 hrs | 250 | Equipment Item | 8 | 2400 | /Equipment Item | 1889 | 4800
[15 empty] | Measure Code |  |  | Incentive per Unit |  | EUL (Years) | SBC Incentive |  | Energy Savings Per Unit | Installation Cost Per Unit
[16 empty] | Cooking Equipment |  |  | Unit |  | Incentive | Unit
[14 empty] | Standard Fat Fryer | CK01 | ENERGY STAR Fat Fryer |  | 200 | Unit | 12 | 200 | /Unit | 1166 | 250
[14 empty] | Standard Steam Cookers | CK02 | ENERGY STAR Steam Cookers |  | 750 | Unit | 12 | 750 | /Unit | 11166 | 937.5
[14 empty] | Standard Hot Food Holding Cabinet (Full-size cabinet) | CK03 | ENERGY STAR Hot Food Holding Cabinet (Full-size cabinet) |  | 300 | Unit | 12 | 300 | /Unit | 2190 | 375
[14 empty] | Standard Hot Food Holding Cabinet (Three-Quarter size cabinet) | CK04 | ENERGY STAR Hot Food Holding Cabinet (Three-Quarter size cabinet) |  | 200 | Unit | 12 | 200 | /Unit | 1642 | 250
[14 empty] | Standard Hot Food Holding Cabinet (Half-size cabinet) | CK05 | ENERGY STAR Hot Food Holding Cabinet (Half-size cabinet) |  | 200 | Unit | 12 | 200 | /Unit | 1095 | 250
[14 empty] | Standard Griddles | CK06 | ENERGY STAR Griddles |  | 250 | Unit | 12 | 250 | /Unit | 2270 | 312.5
[14 empty] | Standard Convection Ovens | CK07 | ENERGY STAR Convection Ovens |  | 350 | Unit | 12 | 350 | /Unit | 2262 | 437.5
[14 empty] | Standard Combination Ovens | CK08 | ENERGY STAR Combination Ovens |  | 1000 | Unit | 12 | 1000 | /Unit | 18431 | 2000
Upgrade & Retrofit
Trade Ally Cost Override?

## R2 HVAC Repl
| HVAC Opportunities | [5 empty] | Sect. 2b
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
FALSE
Enter location, enter number, size, type, and age of HVAC. Report table will autofill. Hide unused lines.
[25 empty] | remove | [5 empty] | hidden | hidden | hidden | [12 empty] | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden |  | doesn't include economizer | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | [11 empty] | hidden | hidden |  | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden
Retrofit Description | [74 empty] | hidden | hidden | hidden | hidden | hidden | hidden
Air conditioning and heating make up a significant portion of your overall energy costs. New high efficiency HVAC units are much more energy efficient than earlier models. | [9 empty] | Replacement HVAC |  | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure. (Indicated by *). Cost entered should be TOTAL cost for the measure. | [21 empty] | Baseline HVAC |  |  | Prescriptive Savings and Incentives | [15 empty] | Custom Savings and Incentives | [28 empty] | For Internal Use Only | [8 empty] | Tier 1 |  |  | Tier 2 |  |  | Tier 1 | Tier 2 | D-E Econ | Tier 1 | Tier 2 |  | Determine Tier
A new HVAC unit will also provide you with quieter operation, better reliability, and superior overall performance. A commercial grade, programmable electronic thermostat designed to work with your new HVAC unit will optimize energy usage while improving temperature control. | [9 empty] | Measure Type | Building Type | [13 empty] | Rated Heating Capacity (Btu/hour) | Equipment Type (Use drop down menu) | Dual Enthalpy Economizer Control (Yes/No) | Total Cost | Annual Operating Hours |  | Efficiency Parameters |  |  | Efficiency Parameters |  |  | Savings Unit |  | Savings D-E Econ |  | Total Savings |  |  | Incentive |  |  | Bonus Incentive |  |  | Total Unit lncentive with Bonus | Total D-E Economizer lncentive with Bonus | Total lncentive | Annual Savings for Custom Measures | [6 empty] | Per Ton/unit Incentive |  |  |  | Initial Incentive Calculation |  |  |  |  | #N/A | Measure Incentive and Savings |  | 0 |  | Custom Incentive (adjusted for Payback and Cap) | Custom Incentive post TRC | Weighted Baseline |  |  | Weighted Efficient |  |  | H Codes |  | HVAC Incremental Cost | AC Only, ASHP Btu category | WSHP, WCAC Btu category | GHP EER category | PTAC, PTHP Btu category | Category |  | Minimum SEER/ IEER | Minimum EER | Minimum HSPF/ COP | Minimum SEER/ IEER | Minimum EER | Minimum HSPF/ COP | H Code | H Code | H Code | Incentive Per Ton | Incentive Per Ton | Determine if HSPF/ COP applies | SEER/ IEER | EER | HSPF/ COP | Identify Relevant Tier for Incentive | Flag for Error message | COP Conversion
Recommedation: Install new high efficiency HVAC unit(s). Units larger than 5 tons should be equipped with an integrated economizer. The existing supply and return air duct system should be rebalanced and all air leakage minimized. | [22 empty] | Age Factor | Condition |  |  |  |  | Cooling | Heating | SEER/ IEER | EER | HSPF/ COP | SEER/ IEER | EER | HSPF/COP | kW | kWh | kW | kWh | kW | kWh | Incentive unit | HVAC Unit | D-E Economizer | Total | Unit Bonus Calculation | D-E Econ Bonus Calculation | Total |  |  |  | kW | kWh | Percent SP (Summer Peak) | Percent SOP (Summer Off Peak) | Percent NSP (Non Summer Peak) | Percent NSOP (Non Summer Off Peak) | Total Percent | Unit | D-E Economizer | Total | Calculated at 0.3 per kWh | 50% of cost limitation | Incentive per HP: Custom (includes failed measures) | Incentive per kWh : Custom (includes failed measures) | Maximum Calculated Incentive | Calculated Incentive Amt (Capped at 50% of Installed Costs) | Incentive Can't Exceed Cost Flag | Payback Period (Years) | Incentive Amount for 1.5 years | "Payback is less than allowed" Flag | Custom Incentive, including any reductions |  |  | SEER/IEER | EER | HSPF/COP | SEER/IEER | EER | HSPF/COP | Unit | D-E Economizer | Btu category | Btu category | Btu category | Btu category | Btu category | Btu category | Unit Lookup Value
Savings Analysis | [9 empty] | 0 |  | Existing HVAC | [15 empty] | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #N/A | #N/A | 0 | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0 | #N/A | #N/A | 0 |  | 0 | 0 | #N/A | #N/A | [5 empty] | 0 | 0 | [8 empty] | 0 | [22 empty] | 0
[31 empty] | Efficiency Parameters | [23 empty] | 0% | 0% | 0% | 0% | 0%
Unit Type | Area served | Qty | Tons Per Unit | Energy savings (kWh) | Electric cost savings | Utility Estimated Cost | PEPCO Incentive | Net Cost to retrofit | Line Item | Measure Type | Building Type | Location of HVAC (Floor/Room) | 0 | 0 | Cooling Capacity BTU/h | 0 | 0 | Tons per Unit | Number of Units | 0 | Type of Unit | Existing Unit Age (years - estimate) | Age Factor | Existing Condition | Rated Heating Capacity (Btu/hour) | Equipment Type (Use drop down menu) | Dual Enthalpy Economizer Control (Yes/No) | Total Cost | Annual Operating HoursCooling | Heating | SEER/ IEER | EE EER | EE HSPF/COP | Baseline SEER/IEER | Baseline EER | Baseline HSPF/COP | Unit Savings kW | Unit Savings kWh | Econ savings kW | Econ savings kWh | Total savings kW | Total savings kWh | Incentive unit | Unit Incentive | Econ Incentive | Total Incentive | Unit Bonus | Econ Bonus | Total Bonus | Total Unit Incentive + Bonus | Total Econ Incentive + Bonus | Total Incentive with bonus | Total savings kW | Total savings kWh | Percent SP (Summer Peak) | Percent SOP (Summer Off Peak) | Percent NSP (Non Summer Peak) | Percent NSOP (Non Summer Off Peak) | Total Percent | custom Unit | custom D-E Economizer | custom Total | custom Calculated at 0.3 per kWh | custom 50% of cost limitation | custom Incentive per HP: Custom (includes failed measures) | custom Incentive per kWh : Custom (includes failed measures) | custom Maximum Calculated Incentive | custom Calculated Incentive Amt (Capped at 50% of Installed Costs) | custom Incentive Can't Exceed Cost Flag | custom Payback Period (Years) | custom Incentive Amount for 1.5 years | custom "Payback is less than allowed" Flag | custom Custom Incentive, including any reductions | Custom Incentive (adjusted for Payback and Cap) | Custom Incentive post TRC | WeightedbaseSEER/IEER | WeightedbaseEER | WeightedbaseHSPF/COP | WeightedEffSEER/IEER | WeightedEffEER | WeightedEffHSPF/COP | Unit Hcode | Econ H Code | HVAC Incremental Cost | AC Only, ASHP Btu category | WSHP, WCAC Btu category |  | PTAC, PTHP Btu category | Category | 0 | Minimum SEER/ IEER | Minimum EER | Minimum HSPF/ COP | Minimum SEER/ IEER | Minimum EER | Minimum HSPF/ COP | H Code | H Code | H Code | Incentive Per Ton | Incentive Per Ton | Determine if HSPF/ COP applies | SEER/ IEER | EER | HSPF/ COP | Identify Relevant Tier for Incentive | Flag for Error message | COP Conversion
|  | 0 | [6 empty] | 1 | [9 empty] | 0 | [6 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | [6 empty] | 2 | [9 empty] | 0 | [6 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | [6 empty] | 3 | [9 empty] | 0 | [6 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 4 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 5 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 6 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 7 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 8 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 9 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 10 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 11 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 12 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 13 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 14 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 15 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 16 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 17 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 18 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 19 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 20 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 21 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 22 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 23 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 24 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 25 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 26 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 27 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 28 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 29 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
|  | 0 | 0 | [5 empty] | 30 | [16 empty] | Single Package | Yes |  | 4000 | 4000 |  |  |  | 0 | 0 | 0 | [8 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | [8 empty] | #N/A | #N/A | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | [22 empty] | No Tier | 0
Totals |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | [35 empty] | 26
[23 empty] | ≤≥ |  |  | 9: Qualifying; 12: Qualifying
[26 empty] | Baseline Unit |  |  | Efficient Tier-1 |  |  | Efficient Tier-2 |  |  | Incentive |  |  | H Code |  |  | Replacement Cost
[17 empty] | Unit |  | Cooling Capacity Size Code | Sub- category | Lookup value | Cooling Capacity Size Category (Btu/h) | Subcategory | Tons |  | SEER / IEER | EER | HSPF / COP | SEER / IEER | EER | HSPF / COP | SEER / IEER | EER | HSPF / COP | Incentive Per Ton Tier 1 | Incentive Per Ton Tier 2 | Dual Enthalpy Economizer Control | Tier 1 | Tier 2 | Dual Enthalpy Economizer Control | Cost Per Ton | ashrae 1989 SEER | ashrae 1989 EER | ashrae 1999 SEER | ashrae 1999 EER | ashrae 2001 SEER | ashrae 2001 EER | ashrae 2004 SEER pre-2006 | ashrae 2004 EER/IPLV (all other heat) | ashrae 2004 SEER post-2006 | ashrae 2007 SEER | ashrae 2007 EER/IPLV (all other heat) | ashrae 2010 SEER | ashrae 2010 EER/IPLV (all other heat) |  |  | Efficiency gain table
[17 empty] | AC Only |  | 1 | Split System | AC Only1Split System | <65,000 | Split System | <5.4 |  | 13 | 11.1 | 0 | 100 | 100 | N/A | 15 | 12.5 | N/A | 35 | 200 | 400 | H1 | SBE-H-PS-022-12 | SBE-H-EC-132-12 | 2200 | 10 |  | 10 |  | 10 |  | 10 |  | 12 | 13 |  | 13 |  |  |  | Unit age | % difference between Std eff today and Std eff at yr X | Efficiency loss due to age | Standard efficiency | oper eff | Efficiency difference
[17 empty] | AC Only |  | 1 | Single Package | AC Only1Single Package | <65,000 | Single Package | <5.4 |  | 13 | 10.9 | 0 | 100 | 100 | N/A | 15 | 12.5 | N/A | 35 | 200 | 400 | H3 | SBE-H-PS-022-12 | SBE-H-EC-132-12 | 2300 | 9.7 |  | 9.7 |  | 9.7 |  | 9.7 |  | 12 | 13 |  | 13 | 11 |  |  | 1 | 0% | 0% | 12 | 12 | 0
[17 empty] | AC Only |  | 2 |  | AC Only2 | ≥ 65,000 and <135,000 | Either | ≥5.4 and <11.25 |  | 11.2 | 11 | 0 | 100 | 100 | N/A | 14 | 12.2 | N/A | 35 | 200 | 400 | H5 | SBE-H-PS-042-12 | SBE-H-EC-132-12 | 1900 |  | 8.9 |  | 10.1 |  | 10.1 |  | 10.1 |  |  | 10.1 |  | 10.8 / 11.0 |  |  | 2 | 0% | 1% | 12 | 11.88 | 1%
[17 empty] | AC Only |  | 3 |  | AC Only3 | ≥135,000 and <240,000 | Either | ≥11.25 and <20 |  | 11 | 10.8 | 0 | 100 | 100 | N/A | 13.2 | 12.2 | N/A | 35 | 200 | 400 | H7 | SBE-H-PS-062-12 | SBE-H-EC-132-12 | 1800 |  | 8.5 |  | 9.5 |  | 9.5 |  | 9.5 |  |  | 9.5 |  | 9.8 / 9.9 |  |  | 3 | 0% | 2% | 12 | 11.76 | 2%
[17 empty] | AC Only |  | 4 |  | AC Only4 | ≥240,000 and <360,000 | Either | ≥20 and <30 |  | 11 | 10.8 | 0 | 100 | 100 | N/A | 12.3 | 10.8 | N/A | 35 | 200 | 400 | H7 | SBE-H-PS-082-12 | SBE-H-EC-132-12 | 1700 |  | 8.5 |  | 9.3 |  | 9.3 / 9.5 |  | 9.3/9.5 |  |  | 9.3/9.5 |  | 9.8 / 9.9 |  |  | 4 | 5% | 3% | 11.4 | 11.058 | 7.85%
[17 empty] | AC Only |  | 5 |  | AC Only5 | ≥360,000 and <600,000 | Either | ≥30 and <50 |  | 9.9 | 9.8 | 0 | 100 | 100 | N/A | 12.3 | 10.8 | N/A | 35 | 200 | 400 | H9 | SBE-H-PS-102-12 | SBE-H-EC-132-12 | 1700 |  | 8.5 |  | 9.3 |  | 9.3 / 9.5 |  | 9.3/9.5 |  |  | 9.3/9.5 |  | 9.8 / 9.9 |  |  | 5 | 9% | 4% | 10.92 | 10.4832 | 12.64%
[17 empty] | AC Only |  | 6 |  | AC Only6 | ≥600,000 and <760,000 | Either | ≥50 and <63.3 |  | 9.9 | 9.8 | 0 | 100 | 100 | N/A | 12 | 10.85 | N/A | 35 | 200 | 400 | H11 | SBE-H-PS-122-12 | SBE-H-EC-132-12 | 1700 |  | 8.5 |  | 9.3 |  | 9.3 / 9.5 |  | 9.3/9.5 |  |  | 9.3/9.5 |  | 9.8 / 9.9 |  |  | 6 | 9% | 5% | 10.92 | 10.374 | 13.55%
[17 empty] | AC Only |  | 7 |  | AC Only7 | ≥760,000 | Either | ≥63.3 |  | 9.6 | 9.5 | 0 | 100 | 100 | N/A | 11.6 | 10.4 | N/A | 35 | 200 | 400 | H21 | SBE-H-PS-142-12 | SBE-H-EC-132-12 | 1700 |  | 8.2 |  | 9 |  | 9.0 / 9.2 |  | 9.0/9.2 |  |  | 9.0/9.2 |  | 9.5 / 9.6 |  |  | 7 | 9% | 6% | 10.92 | 10.2648 | 14.46%
[57 empty] | 8 | 13% | 6% | 10.44 | 9.8136 | 18.22% | bar: 6 to 8; 12 to 14; 16 to 17; 19 to 21
[17 empty] | ASHP |  | 1 | Split System | ASHP1Split System | <65,000 | Split System | <5.4 |  | 13 | 11.1 | 7.9 | 100 | 100 | 100 | 15 | 12.5 | 8.6 | 35 | 200 | 400 | H1 | SBE-H-PS-022-12 | SBE-H-EC-132-12 | 2200 | 10 |  | 10 |  | 10 | 10 | 10 | 12.1 | 12 | 13 |  | 13 |  |  |  | 9 | 13% | 7% | 10.44 | 9.7092 | 19.09%
[17 empty] | ASHP |  | 1 | Single Package | ASHP1Single Package | <65,000 | Single Package | <5.4 |  | 13 | 10.9 | 7.7 | 100 | 100 | 100 | 15 | 12.5 | 8.5 | 35 | 200 | 400 | H3 | SBE-H-PS-022-12 | SBE-H-EC-132-12 | 2300 | 9.7 |  | 9.7 |  | 9.7 | 9.7 | 9.7 | 12.1 | 12 | 13 |  | 13 |  |  |  | 10 | 17% | 8% | 9.96 | 9.1632 | 23.64%
[17 empty] | ASHP |  | 2 |  | ASHP2 | ≥ 65,000 and <135,000 | Either | ≥5.4 and <11.25 |  | 11.2 | 11 | 3.3 | 100 | 100 | 100 | 14 | 12.2 | 4.6 | 35 | 200 | 400 | H5 | SBE-H-PS-042-12 | SBE-H-EC-132-12 | 1900 |  | 8.5 |  | 10.1 |  | 9.9 |  | 9.9 |  |  | 9.9 |  | 10.8 / 11.0 |  |  | 11 | 21% | 9% | 9.48 | 8.6268 | 28.11%
[17 empty] | ASHP |  | 3 |  | ASHP3 | ≥135,000 and <240,000 | Either | ≥11.25 and <20 |  | 11 | 10.8 | 3.2 | 100 | 100 | 100 | 13.2 | 12.2 | 4.4 | 35 | 200 | 400 | H7 | SBE-H-PS-062-12 | SBE-H-EC-132-12 | 1800 |  | 8.3 |  | 9.1 |  | 9.1 |  | 9.1 |  |  | 9.1 |  | 10.4 / 10.5 |  |  | 12 | 23% | 10% | 9.24 | 8.316 | 30.7%
[17 empty] | ASHP |  | 3 |  | ASHP3 | ≥240,000 and <360,000 | Either | ≥20 and <30 |  | 11 | 10.8 | 3.2 | 100 | 100 | 100 | 12.3 | 10.8 | 4.4 | 35 | 200 | 400 | H7 | SBE-H-PS-082-12 | SBE-H-EC-132-12 | 1700 |  | 8.3 |  | 8.8 |  | 8.8 / 9.0 |  | 8.8 / 9.0 |  |  | 8.8 / 9.0 |  | 10.4 / 10.5 |  |  | 13 | 35% | 11% | 7.8 | 6.942 | 42.15%
[17 empty] | ASHP |  | 4 |  | ASHP4 | ≥360,000 and <600,000 | Either | ≥30 and <50 |  | 9.9 | 9.8 | 3.2 | 100 | 100 | 100 | 12.3 | 10.8 | 4.2 | 35 | 200 | 400 | H9 | SBE-H-PS-102-12 | SBE-H-EC-132-12 | 1700 |  | 8.3 |  | 8.8 |  | 8.8 / 9.0 |  | 8.8 / 9.0 |  |  | 8.8 / 9.0 |  | 10.4 / 10.5 |  |  | 14 | 36% | 13% | 7.68 | 6.6816 | 44.32%
[17 empty] | ASHP |  | 5 |  | ASHP5 | ≥600,000 and <760,000 | Either | ≥50 and <63.3 |  | 9.9 | 9.8 | 3.2 | 100 | 100 | 100 | 12 | 10.85 | 3.8 | 35 | 200 | 400 | H11 | SBE-H-PS-122-12 | SBE-H-EC-132-12 | 1700 |  | 8.3 |  | 8.8 |  | 8.8 / 9.0 |  | 8.8 / 9.0 |  |  | 8.8 / 9.0 |  | 10.4 / 10.5 |  |  | 15 | 36% | 15% | 7.68 | 6.528 | 45.6%
[17 empty] | ASHP |  | 6 |  | ASHP6 | ≥760,000 | Either | ≥63.3 |  | 9.6 | 9.5 | 3.2 | 100 | 100 | 100 | 11.6 | 10.4 | 3.6 | 35 | 200 | 400 | H21 | SBE-H-PS-142-12 | SBE-H-EC-132-12 | 1700 |  | 8.5 |  | 8.8 |  | 8.8 / 9.0 |  | 8.8 / 9.0 |  |  | 8.8 / 9.0 |  | 9.3 / 9.4 |  |  | 16 | 38% | 17% | 7.44 | 6.1752 | 48.54%
[57 empty] | 17 | 39% | 18% | 7.32 | 6.0024 | 49.98% | bar: 6 to 8; 12 to 14; 21
[17 empty] | WSHP |  | 1 |  | WSHP1 | <65,000 | Single Package | <5.4 |  | 12 | 12 | 4.2 | 100 | 100 | 100 | 14 | 14 | 4.7 | 50 | 200 |  | H14 | SBE-H-WE-142-12 |  | 1400 |  | 9.3 |  | 12 |  | 11.2 |  | 12 |  |  | 11.2 OR 12 | 11.2 OR 12 |  |  |  | >17 | 39% | 18% | 7.32 | 6.0024 | 49.98%
[17 empty] | WSHP |  | 2 |  | WSHP2 | ≥65,000 and <135,000 | Single Package | ≥5.4 and <11.25 |  | 12 | 12 | 4.2 | 100 | 100 | 100 | 14 | 14 | 4.7 | 50 | 200 |  | H15 | SBE-H-WE-152-12 |  | 1300 |  | 10.5 |  | 12 |  | 12 |  | 12 |  |  | 12.2 |  | 12
[17 empty] | WSHP |  | 3 |  | WSHP3 | ≥135,000 | Single Package | ≥11.25 |  | 11.3 | 11.3 | 4 | 100 | 100 | 100 | 14 | 14 | 4.7 | 50 | 200 |  | H16 | SBE-H-WE-162-12 |  | 1200 |  | NA |  | NA |  | NA |  | NA |  |  | NA |  | NA
[17 empty] | WCAC |  | 1 |  | WCAC1 | <65,000 | Single Package | <5.4 |  | 12.1 | 12.1 | N/A | 100 | 100 | 100 | 14 | 14 | N/A | 50 | 200 | 400 | H14 | SBE-H-WE-142-12 | SBE-H-EC-132-12 | 1400
[17 empty] | WCAC |  | 2 |  | WCAC2 | ≥65,000 and <135,000 | Single Package | ≥5.4 and <11.25 |  | 11.5 | 11.5 | N/A | 100 | 100 | 100 | 14 | 14 | N/A | 50 | 200 | 400 | H15 | SBE-H-WE-152-12 | SBE-H-EC-132-12 | 1300 |  | 9.3 |  | 12.1 |  | 12.1 |  | 12.1 |  |  | 12.1 |  | 12.1 / 12.3
[17 empty] | WCAC |  | 3 |  | WCAC3 | ≥135,000 | Single Package | ≥11.25 |  | 11.3 | 11.3 | N/A | 100 | 100 | 100 | 14 | 14 | N/A | 50 | 200 | 400 | H16 | SBE-H-WE-162-12 | SBE-H-EC-132-12 | 1200 |  | 10.5 |  | 11.3 |  | 11.3 |  | 11.3 |  |  | 11.3 |  | 11.9 / 12.1
[26 empty] | 23: 9.6; 25: 11 |  | 10.8 |  | 10.8/10.1 |  |  | 10.8 |  | 12.3 / 12.5
[17 empty] | GHP |  | 1 |  | GHP1 | All | Single Package |  |  | 15 | 15 | 4 | 100 | 100 | 100 | 18 | 18 | 4.7 | 40 | 200 |  |  | SBE-H-GS-242-12 |  | 1700 |  | 9.6 |  | 11 |  | 10.8 / 10.1 |  | 10.8/10.1 |  |  | 10.8/10.1 |  | 12.2 / 12.4
[17 empty] | GHP |  | 2 |  | GHP2 | All | Single Package |  |  | 15 | 15 | 4 | 100 | 100 | 100 | 20 | 20 | 5 | 40 | 500 |  |  | SBE-H-GS-252-12 |  | 1700
[26 empty] | 23: 11 |  | 13.4 |  | 13.4 |  |  | 13.4 |  | 13.4
[17 empty] | PTAC |  | 1 |  | PTAC1 |  | Single Package | < 3/4 Ton |  | 8.6 | 8.6 | N/A | 100 | 100 | 100 | 11.8 | 11.8 | N/A | 40 | 80 |  | H17 | SBE-H-TA-172-12 |  | 1700
[17 empty] | PTAC |  | 2 |  | PTAC2 |  | Single Package | ≥ 3/4 ton and < 1 ton |  | 8.6 | 8.6 | N/A | 100 | 100 | 100 | 11 | 11 | N/A |  | 80 |  |  | SBE-H-TA-173-12 |  | 1700
[17 empty] | PTAC |  | 3 |  | PTAC3 |  | Single Package | 1 Ton and greater |  | 8.2 | 8.2 | N/A | 100 | 100 | 100 | 10.3 | 10.3 | N/A | 50 | 100 |  | H19 | SBE-H-TA-192-12 |  | 1700 |  | 10-(0.16*Btuh/1000) |  | 12.5-(0.213*Btuh/1000) |  |  | 10.9-(0.213*Btuh/1000) | 10.9-(0.213*Btuh/1000) |  |  | 10.9-(0.213*Btuh/1000) |  | 9.7
[17 empty] | PTHP |  | 1 |  | PTHP1 |  | Single Package | < 3/4 Ton |  | 8.5 | 8.5 | 2.6 | 100 | 100 | 100 | 11.5 | 11.5 | 3.3 | 40 | 100 |  | H18 | SBE-H-TH-182-12 |  | 1700 |  | 10-(0.16*Btuh/1000) |  | 12.5-(0.213*Btuh/1000) |  |  | 10.9-(0.213*Btuh/1000) | 10.9-(0.213*Btuh/1000) |  |  | 10.9-(0.213*Btuh/1000) |  | 9.8
[17 empty] | PTHP |  | 2 |  | PTHP2 |  | Single Package | ≥ 3/4 ton and < 1 ton |  | 8.5 | 8.5 | 2.6 | 100 | 100 | 100 | 10.8 | 10.8 | 3.2 |  | 100 |  |  | SBE-H-TH-183-12 |  | 1700 |  | 10-(0.16*Btuh/1000) |  | 12.5-(0.213*Btuh/1000) |  |  | 10.9-(0.213*Btuh/1000) | 10.9-(0.213*Btuh/1000) |  |  | 10.9-(0.213*Btuh/1000) |  | 9.7
[17 empty] | PTHP |  | 3 |  | PTHP3 |  | Single Package | 1 Ton and greater |  | 8.1 | 8.1 | 2.5 | 100 | 100 | 100 | 10.1 | 10.1 | 3.1 | 50 | 120 |  | H20 | SBE-H-TH-202-12 |  | 1700 |  | 10-(0.16*Btuh/1000) |  | 12.5-(0.213*Btuh/1000) |  |  | 10.9-(0.213*Btuh/1000) | 10.9-(0.213*Btuh/1000) |  |  | 10.9-(0.213*Btuh/1000) |  | 8.5
[17 empty] | DACHP |  |  |  | DACHP | All | Split System |  |  | 15 | 15 | N/A | 100 | 100 | 100 | 16 | 16 | N/A |  | 200 |  |  | SBE-H-DM-262-12 |  | 1700 |  | 10-(0.16*Btuh/1000) |  | 12.5-(0.213*Btuh/1000) |  |  | 10.8-(0.213*Btuh/1000) | 10.8-(0.213*Btuh/1000) |  |  | 10.8-(0.213*Btuh/1000) |  | 9
[26 empty] | 23: 10-(0.16*Btuh/1000); 25: 12.5-(0.213*Btuh/1000) |  |  | 10.8-(0.213*Btuh/1000) | 10.8-(0.213*Btuh/1000) |  |  | 10.8-(0.213*Btuh/1000) |  | 9
[26 empty] | 23: 10-(0.16*Btuh/1000); 25: 12.5-(0.213*Btuh/1000) |  |  | 10.8-(0.213*Btuh/1000) | 10.8-(0.213*Btuh/1000) |  |  | 10.8-(0.213*Btuh/1000) |  | 9
[22 empty] | Coincidence Factor: | 0.923
[22 empty] | EUL: | 15 |  |  | 6: Incentive:; 23: NR; 25: NR | [8 empty] | NA
[19 empty] | Yes/No | Condition? | [5 empty] | 6: AC / ASHP:
[17 empty] | Yes |  | Yes | Good |  |  | Type of Unit: |  |  | 6: Tier 1; 7: $35/ton
[17 empty] | No |  | No | Fair |  | AC Only | AC Only |  |  | 6: Tier 2; 7: $70/ton
[20 empty] | Poor |  | Air Source Heat Pump | ASHP |  |  | 6: WSHP / WCAC:
[17 empty] | Split System |  |  |  |  | Water Source Heat Pump | WSHP |  |  | 6: All:; 7: $50/ton
[17 empty] | Single Package |  |  |  |  | Water Cooled Air Conditioning | WCAC |  |  | 6: PTAC / PTHP:
[22 empty] | Geothermal Heat Pump | GHP |  |  | 6: < 1.0 ton; 7: $40/unit
[22 empty] | Packaged Terminal Air Conditioner | PTAC |  |  | 6: >/= 1.0 ton; 7: $50/unit
[17 empty] | Bonus |  | 0% |  |  | Packaged Terminal Heat Pump | PTHP
[22 empty] | Ductless, Mini-Split AC or HP | DACHP |  |  | 19: Subcategory
Split System
[22 empty] | Annual Operating Hours Adjustment | 65% |  |  | 19: Single Package
[22 empty] | COP Conversion Factor | 3.412
[22 empty] | Cost: <65000 Btu | 1700 | per ton
[22 empty] | Cost: >=65000 Btu | 1700 | per ton
[17 empty] | Put these in the DD |  | Standard list | SAVdee
[17 empty] | Grocery Stores |  | Grocery | 139
[17 empty] | Large grocery store chain |  | Grocery | 139
[17 empty] | Convenience store |  | Grocery | 139
[17 empty] | Hospitals |  | Health | 56
[17 empty] | Ambulatory health care |  | Health | 56
[17 empty] | Nursing or residential care |  | Health | 56
[17 empty] | College or University |  | Higher Education | 171
[17 empty] | Fabrication |  | Industrial | 23
[17 empty] | Process |  | Industrial | 23
[17 empty] | Heavy manufacturing |  | Industrial | 23
[17 empty] | Warehouse |  | Industrial | 23
[17 empty] | Laboratories |  | Industrial | 23
[17 empty] | Biotech |  | Industrial | 23
[17 empty] | Farms |  | Industrial | 23
[17 empty] | Dairies |  | Industrial | 23
[17 empty] | Livestock farm |  | Industrial | 23
[17 empty] | Greenhouse |  | Industrial | 23
[17 empty] | Refrigerated Warehouse |  | Industrial | 23
[17 empty] | Food Processor |  | Industrial | 23
[17 empty] | Data Center |  | Industrial | 23
[17 empty] | Hospitality/Lodging |  | Lodging | 56
[17 empty] | Assisted Living |  | Lodging | 56
[17 empty] | Nursing or residential care |  | Lodging | 56
[17 empty] | Multifamily |  | Multi-Family | 56
[17 empty] | Office building |  | Office | 171
[17 empty] | Small office |  | Office | 171
[17 empty] | Large Non-Profit |  | Office | 171
[17 empty] | Small Non-Profit |  | Office | 171
[17 empty] | Federal |  | Office | 171
[17 empty] | State |  | Office | 171
[17 empty] | County |  | Office | 171
[17 empty] | Municipality |  | Office | 171
[17 empty] | Large Faith-Based |  | Religious | 6
[17 empty] | Small Faith-Based |  | Religious | 6
[17 empty] | Food Services |  | Restaurant | 36
[17 empty] | Restaurants |  | Restaurant | 28
[17 empty] | Big Box Retail |  | Retail | 171
[17 empty] | General retail |  | Retail | 171
[17 empty] | Small Retail |  | Retail | 87
[17 empty] | Car dealerships |  | Retail | 87
[17 empty] | School |  | School | 39
[17 empty] | Warehouse |  | Warehouse | 2
[17 empty] | Other |  | Other | 56
[17 empty] | Percent SP (Summer Peak) |  | Percent SOP (Summer Off Peak) | Percent NSP (Non Summer Peak) | Percent NSOP (Non Summer Off Peak) | Total Percent
[17 empty] | 65% |  | 20% | 15% | 0% | 100%
Includes measures that failed B/C test
[17 empty] | Total Custom kW |  |  | 1.5
[17 empty] | Total Custom kWh |  |  | 138.96
Note: These calculations are here so as not to create circular references to remove failed measures from totals.
[17 empty] | kWh incentive |  |  |  | 0.3 | /kWh
[17 empty] | Average_Cost_Electricity |  |  |  | 0.15 | /kWh
[17 empty] | Minimum_Payback_Period |  |  |  | 1.5 | years
Note: Highlighted incentive has been reduced--custom incentives cannot exceed project cost and payback period cannot be less than 1.5 years
Note: Highlighted incentive has been reduced-- custom incentives cannot exceed 50% of project costs
Note: Highlighted incentive has been reduced--payback period cannot be less than 1.5 years
New Measure Codes
From Bob's table
[19 empty] | HV02 | E-H-PS-022-12 | HVAC | Packaged/Split A/Cs Air Source Heat Pumps | < 5.4 tons
[19 empty] | HV03 | E-H-PS-032-12 | HVAC | [Reserved for possible future use]
[19 empty] | HV04 | E-H-PS-042-12 | HVAC | Packaged/Split A/Cand Air Source Heat Pumps | >/= 5.4 and < 11.25 tons
[19 empty] | HV05 | E-H-PS-052-12 | HVAC | [Reserved for possible future use]
[19 empty] | HV06 | E-H-PS-062-12 | HVAC | Packaged/Split A/Cs and Air Source Heat Pumps | >/= 11.25 and < 20 tons
[19 empty] | HV07 | E-H-PS-072-12 | HVAC | [Reserved for possible future use]
[19 empty] | HV08 | E-H-PS-082-12 | HVAC | Packaged/Split A/Cs and Air Source Heat Pumps | >/= 20 and < 30 tons
[19 empty] | HV09 | E-H-PS-092-12 | HVAC | [Reserved for possible future use]
[19 empty] | HV10 | E-H-PS-102-12 | HVAC | Packaged/Split A/C and Air Source Heat Pumps | >30 < 50 tons
[19 empty] | HV11 | E-H-PS-112-12 | HVAC | [Reserved for possible future use]
[19 empty] | HV12 | E-H-PS-122-12 | HVAC | Packaged/Split A/C and Air Source Heat Pumps | >50 < 63.3 tons
[19 empty] | HV13 | E-H-PS-132-12 | HVAC | [Reserved for possible future use]
[19 empty] | HV27 | E-H-EC-132-12 | HVAC | Dual Enthalpy Economizer Control | On new HVAC unit meeting minimum requirements
[19 empty] | HV15 | E-H-WE-142-12 | HVAC | Pkg'd/Split A/Cs and HPs | Water- and Evaporative cooled condensers
[19 empty] | HV16 | E-H-WE-152-12 | HVAC | Pkg'd/Split A/Cs and HPs | Water- and Evaporative cooled condensers
[19 empty] | HV17 | E-H-WE-162-12 | HVAC | Packaged/Split Air Conditioners and Heat Pumps | Water- and Evaporative cooled condensers
[19 empty] | HV20 | E-H-TA-172-12 | HVAC | PTAC - Single Package | < 3/4 ton
[19 empty] | HV21 | E-H-TA-173-12 | HVAC | PTAC - Single Package | >/= 3/4 and < 1 ton
[19 empty] | HV23 | E-H-TH-182-12 | HVAC | PTHP - Single Package | < 3/4 ton
[19 empty] | HV24 | E-H-TH-183-12 | HVAC | PTHP - Single Package | >/= 3/4 and < 1 ton
[19 empty] | HV22 | E-H-TA-192-12 | HVAC | PTAC - Single Package | >/= 1 ton
[19 empty] | HV25 | E-H-TH-202-12 | HVAC | PTHP - Single Package | >/= 1 ton
[19 empty] | HV14 | E-H-PS-142-12 | HVAC | Packaged/Split A/C and Air Source Heat Pumps | >/= 63.3 tons
[19 empty] | HV15 | E-H-PS-152-12 | HVAC | [Reserved for possible future use]
[19 empty] | HV18 | E-H-GS-242-12 | HVAC | Geothermal Heat Pumps | 18 EER or greater
[19 empty] | HV19 | E-H-GS-252-12 | HVAC | [Reserved for possible future use]
[19 empty] | HV26 | E-H-DM-262-12 | HVAC | Ductless, Mini-Split A/C and Heat Pumps
#REF!
Measure Cost-Effectiveness Tool (2012 version)
Assumptions
Utility discount rate
[20 empty] | Program | Non-Residential Custom
Net-to-Gross ratio
[20 empty] | Measure | HVAC
Measure Life
[20 empty] | Incentive Cost | 0
Non-Incentive Cost
[21 empty] | Cost | Annualized Energy Usage |  |  |  | 7: Demand; 9: Gas
[21 empty] | Measure Cost | SP kWh | SOP kWh | NSP kWh | NSOP kWh | 6: Total kWh; 7: Adjustment Factor; 8: Peak Demand kW Savings; 9: Gas therms
[20 empty] | Base | [5 empty] | 6: 0; 8: #VALUE!
[20 empty] | Savings Distribution (%) |  | 0% | 0% | 0% | 0% | 6: 0%; 8: 0
[21 empty] | 0 | 0 | 0 | 0 | 0 | 6: 138.96; 8: 1.5; 9: 0
Summary
TRC
Prepared by:
[20 empty] | Date: | 2012-11-14 13:59 |  |  |  |  | 8: Tool Version Date:; 9: 2012-01-17
[20 empty] | Notes: | See "Measures" tab for typical Measure names and lives
TRC includes line losses and is calculated at the generator level
Benefit Cost Flag
0
3-1
Air Conditioning
3-1
3-1
3-1
New Efficient HVAC Unit
Trade Ally Cost Override?
Note on DG11: jarichter: I had originally evaluated the HSPF/COP to identify relevant incentive Tier. However, per Bill Steigelmann on 9/12/2011, this should not be. In the event this changes in the future, I kept the formulas as is, except that I always make HSPF/COP Tier 2 so it will pass. If we decide to evaluate on HSPF/COP then this column will have to change to identify actual Tier.
Note on BI12: 7 AM - 11 PM weekdays (except holidays), June through September
Note on BJ12: All other hours during June through September
Note on BK12: 7 AM - 11 PM weekdays (except holidays), October through May
Note on BL12: All other hours during October through May
Note on BS12: jarichter: These values are used in the TRC calculation
Note on BT12: jarichter: Also calculate incentive as if this were a strictly custom measure, that is, at $0.16/kWh and then if it's higher then this feeds into the TRC tool.
Note on BZ12: jarichter: this zeros out the toggle if the measure is prescriptive as currently we're not doing the payback test on prescriptive measures.. If that changes, we'll need to Total Incentive column to not look at the Incentive Basis column.
Note on AK50: jarichter: 2012- No longer use Tier 1, but leaving the columns just in case we need it again. Currently these data are not used.
Note on AO52: jarichter: 2012 - no longer in use
Note on AR52: jarichter: 2012 - no longer in use
Note on AH78: jarichter: tentative values per Bill 3-6-2012
Note on AN78: jarichter: tentative values per Bill 3-7-2012
Note on AH79: jarichter: tentative values per Bill 3-6-2012
Note on AN79: jarichter: tentative values per Bill 3-7-2012
Note on W158: 7 AM - 11 PM weekdays (except holidays), June through September
Note on Y158: All other hours during June through September
Note on Z158: 7 AM - 11 PM weekdays (except holidays), October through May
Note on AA158: All other hours during October through May
Note on AA220: Starting in 2012

## R2 VFD (hidden)
Variable Frequency Drives | [5 empty] | Sect. 2c | [45 empty] | End Use / Motor Type | Default Hrs/Year | Default Use Factor | Load Factor | Fan or Pump? | Measure Type | Submenu | ESF | DSF
[7 empty] | Copyright © 2012 Potomac Electric Power Company |  | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure. (Indicated by *). Cost entered should be TOTAL cost for the measure. | [42 empty] | Air Compressor | 576 | 100% | 70% | Other | Alternative
[7 empty] | All Rights Reserved | [44 empty] | Air Conditioning Chiller Compressor | 3300 | 100% | 80% | Other | Alternative
[52 empty] | Boiler Draft Fan | 3300 | 100% | 80% | Fan | Prescriptive | Fan_Type | 0.475 | 0.349
Measure Description | [51 empty] | Boiler Feedwater Pump | 3844 | 100% | 80% | Pump | Prescriptive |  | 0.646 | 0
Variable Frequency Drives save energy by slowing motors to a speed that matches the actual needs of an application at any given time. Without VFDs, motors typically run full speed with some form of throttling or cycling to reduce the work performed. This wastes a lot of energy. Energy saved by VFDs can be significant - reducing motor speed to 80% of full load typically saves 50% of the energy used at full load! | [51 empty] | Building Exhaust Fan | 3300 | 100% | 80% | Fan | Alternative | Fan_Type
Recommendation | [8 empty] | Select End Use Category, Motor Horsepower and Quantity. If measure type comes up as "alternative" energy savings must be entered manually under the "Alternative Measures Only" heading. For prescriptive measures leave those cells blank. | [6 empty] | FALSE | [35 empty] | Chilled Water (ChW) Pump | 3844 | 100% | 80% | Pump | Prescriptive |  | 0.58 | 0.401
PEPCO offers generous small business incentives for installation of VFDs on motors over 2HP in a variety of applications. Install Variable Frequency Drives in the following locations: | [51 empty] | Condensate Pump (for AC) | 3844 | 100% | 80% | Pump | Prescriptive |  | 0.2 | 1
Project Summary | Qty | HP | Annual Electrical Savings (kWh) | Annual Cost Savings | Utility Estimated Cost | PEPCO Incentive | Net Project Cost | [18 empty] | to det. motor eff & pf if not available | [5 empty] | Full Load | Motor load as | [5 empty] | Default Values |  |  |  | SUMMARY TABLE for 1800 RPM, General Purpose, TEFC, NEMA Design B Motors, >=1 hp PF Extracted from MotorMaster 4/9/98, < 1 hp from Grainger #388 1997, GE List | [8 empty] | Condensate Pump (steam system) | 3844 | 100% | 80% | Pump | Prescriptive |  | 0.646 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | Volts | Amps | [6 empty] | From Motor Label |  | Prem Eff? | Estimated |  | Est | Est | Power |  | Input Power | a % of full | operating | Use |  | annual kWh |  |  |  | Default | Motor load | [9 empty] | Condenser Water Pump | 3844 | 100% | 80% | Pump | Prescriptive |  | 0.58 | 0.401
[9 empty] | Enduse Category |  | Alternative Measures Only |  | Motor HP | Qty | (Measured) | (Measured) | Phase | Measure Code | Pump or Fan | ESF | DSF | CF | Efficiency | PF | (Select One) | BHP | HP | motor eff | pf | Factor | Motor Eff | kW | load power | kW | Factor | hrs/yr | each motor | total kW |  | Default | Use | as a % of | [9 empty] | Cooling Tower Fan | 3300 | 100% | 80% | Fan | Prescriptive | Fan_Type | 0.475 | 0.349
End use description | Qty | HP | Annual Electrical Savings (kWh) | Annual Cost Savings | Utility Estimated Cost | PEPCO Incentive | Net Project Cost |  | (Select from Dropdown Menu) | Measure Type (will autofill) | kW Reduction | Annual kWh Reduction | (Select from Dropdown Menu) | [25 empty] | End-use categories | Hr/yr | Factor | max rated load |  |  | Motor Efficiency |  | Motor Power Factor |  | Est. Installed VFD Cost | Incentive | Measure Code | Domestic Water Booster Pump | 3844 | 100% | 80% | Pump | Alternative
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | 24 hour use | 8760 | 100% | 75% |  | HP | Std | Prem. | Std | Prem. |  |  |  | Domestic Water Circ Pump | 3844 | 100% | 80% | Pump | Alternative
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Air Compressor | 576 | 100% | 70% |  | 0.25 | 62.7% | 67.5% | 53.33% | 57.8% |  |  | TBD | Hot Water Pump | 3844 | 100% | 80% | Pump | Prescriptive |  | 0.646 | 0
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Air handlers-vfd controlled | 3844 | 45% | 90% |  | 0.33 | 66% | 68.8% | 62.42% | 64.16% |  |  | TBD | HVAC Exhaust Fan | 3300 | 100% | 80% | Fan | Prescriptive | Fan_Type | 0.475 | 0.349
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Elevator & other | 4800 | 47.32% | 70% |  | 0.5 | 69% | 73.9% | 61.68% | 63.35% |  |  | TBD | HVAC Return Air Fan | 3300 | 100% | 80% | Fan | Prescriptive | Fan_Type | 0.475 | 0.349
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Escalator | 5538 | 100% | 80% |  | 0.75 | 76% | 78.5% | 66% | 74.55% |  |  | TBD | HVAC Supply Air Fan | 3300 | 100% | 80% | Fan | Prescriptive | Fan_Type | 0.475 | 0.349
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Exhaust Fans | 3300 | 100% | 80% |  | 1 | 82.04% | 84.59% | 72.5% | 76.5% |  |  | TBD | Make-Up Air Fan | 3300 | 100% | 80% | Fan | Prescriptive | Fan_Type | 0.475 | 0.349
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | HVAC unit-supply fan | 3300 | 100% | 90% |  | 1.5 | 83.67% | 85.83% | 72.9% | 77.2% |  |  | TBD | Other |  |  |  | Other | Alternative
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | HVAC-supply fan cycles | 2100 | 100% | 90% |  | 2 | 83.73% | 85.98% | 76.9% | 78.8% | 3000 | 1500 | SBVFD1 | Pool Pump | 3844 | 100% | 80% | Pump | Alternative
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Miscellaneous High Use | 6700 | 100% | 85% |  | 3 | 86.12% | 88.54% | 78.1% | 80% | 3000 | 1500 | SBVFD2 | Process Cooling Pump | 3844 | 100% | 80% | Pump | Alternative
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Miscellaneous Low Use | 1000 | 100% | 70% |  | 4 |  |  |  |  | 3000 | 1500 | SBVFD3 | Process Exhaust Fan or Fume Hood | 3300 | 100% | 80% | Fan | Alternative | Fan_Type
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Process use | 5850 | 90% | 70% |  | 5 | 86.81% | 88.47% | 82.2% | 83.2% | 3200 | 1600 | SBVFD4 | Transfer Pump | 3844 | 100% | 80% | Pump | Alternative
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Pumps, constant load | 3843.84 | 100% | 80% |  | 7.5 | 88.16% | 90.08% | 83.1% | 83.4% | 3600 | 1800 | SBVFD5 | Wastewater Pump | 3844 | 100% | 80% | Pump | Alternative
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Pumps, variable load | 3844 | 60% | 80% |  | 10 | 89.25% | 90.58% | 84% | 85.2% | 4000 | 2000 | SBVFD6 | Well Pump | 3844 | 100% | 80% | Pump | Custom
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | other-20% Use Factor | 8760 | 20% | 80% |  | 15 | 90.02% | 91.37% | 84.7% | 84.7% | 4600 | 2300 | SBVFD7 | WSHP Circ Loop Pump | 3844 | 100% | 80% | Pump | Prescriptive |  | 0.2 | 1
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | other-50% Use Factor | 8760 | 50% | 80% |  | 20 | 90.13% | 91.7% | 86% | 85.5% | 5000 | 2500 | SBVFD8
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | other-80% Use Factor | 8760 | 80% | 80% |  | 25 | 91.73% | 92.57% | 85.9% | 85.8% | 6000 | 3000 | SBVFD9
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | Use factor-loads that are constant are generally figured at 100% |  |  |  |  | 30 | 91.55% | 92.57% | 87.2% | 86.4% | 7000 | 3500 | SBVFD10
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | loads that are variable do not use full load power at all hours |  |  |  |  | 40 | 91.86% | 93.04% | 86% | 85.6% | 8000 | 4000 | SBVFD11
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | of operation, therefore the use factor is less than 100% |  |  |  |  | 50 | 91.87% | 93.01% | 85.6% | 85.9% | 9000 | 4500 | SBVFD12
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | [5 empty] | 60 | 92.8% | 93.48% | 87.3% | 85.8% | 10800 | $0.30 / kWh | SBVFD13
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | [5 empty] | 75 | 93.01% | 93.5% | 87.7% | 86.8% | 13500 | $0.30 / kWh | SBVFD13
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | [5 empty] | 100 | 93.19% | 93.77% | 87.8% | 86.3% | 18000 | $0.30 / kWh | SBVFD13 | HVAC Fan VFD Savings Factors
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | [5 empty] | 125 | 93.1% | 93.88% | 88.6% | 86.8% | 22500 | $0.30 / kWh | SBVFD13 | Fan Design | ESF | DSF
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | [5 empty] | 150 | 93.47% | 94.24% | 88.8% | 86.9% | 27000 | $0.30 / kWh | SBVFD13 | Constant Volume | 0.717 | 0.466
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | [5 empty] | 200 | 93.61% | 94.4% | 88.3% | 86.7% | 36000 | $0.30 / kWh | SBVFD13 | Air foil / Backward Incline (AF/BI) | 0.475 | 0.349
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | [5 empty] | 300 | 95.3% | 95.8% | 90.4% | 86.8% | 54000 | $0.30 / kWh | SBVFD13 | AF/BI Inlet guide vanes | 0.304 | 0.174
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | [5 empty] | 350 | 95.4% | 95.9% | 89.3% | 88.8% | 63000 | $0.30 / kWh | SBVFD13 | Forward curved | 0.24 | 0.182
0 |  | 0 | [16 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | #VALUE! | [5 empty] | 400 | 95.3% | 95.6% | 89.4% | 86.9% | 72000 | $0.30 / kWh | SBVFD13 | FC Inlet guide vanes | 0.123 | 0.039
[19 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | 0 | [5 empty] | 450 | 95% | 95% | 90% | 90% | 81000 | $0.30 / kWh | SBVFD13
[19 empty] | #N/A | #N/A | #N/A | #N/A |  |  | No | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | 0% | 0 | 0% | 0 | 0 | 0 | [5 empty] | 500 | 95.2% | 95.2% | 90.5% | 90.5% | 90000 | $0.30 / kWh | SBVFD13 | HVAC Pump VFD Savings Factors
[52 empty] | Chilled Water Pump | 0.58 | 0.401
[52 empty] | Hot Water Pump | 0.646 | 0
[55 empty] | Other |  |  | 0%
[55 empty] | Water |  |  | 0%
[57 empty] | HVAC Equipment Efficiency - New | 20
[57 empty] | HVAC Quality Installation - Existing | 3
[57 empty] | HVAC Quality Installation - New | 3
[55 empty] | Utility discount rate | 8.18%
[8 empty] | 0 | [43 empty] | 0 | Incentive per HP
[52 empty] | 0.3 | Incentive per kWh
[52 empty] | 0.746 | HP to kW conversion factor
[52 empty] | 0.55 | CF for Pumps
[52 empty] | 0.28 | CF for Fans
[52 empty] | Type | Pepco List |  | Potomac List | TRM- Mid-Atlantic | NY Manual | ESF | DSF | Pump or Fan | Submenu | Prescriptive
[52 empty] | Building Exhaust Fan | x |  | x |  |  | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | Make-up Air Fan | x |  |  |  | x | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | Process Exhaust |  |  |  |  | x | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | HVAC Return Air Fan | x |  |  |  |  | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | HVAC Exhaust Fan |  |  |  |  | x | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | Cooling Tower Fan | x |  | x |  | x | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | HVAC Supply Air Fan | x |  |  |  |  | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | AHU Supply and Return Fans |  |  |  |  | x | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | Process Fan | x |  | x |  |  | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | Boiler Draft Fan |  |  | x |  | x | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | HVAC Fan |  |  | x |  |  | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | Other Fan |  |  | x |  |  | 1 | 1 | Fan | Fan_Type | Custom
[52 empty] | Chilled/Condenser Water Pump | x |  |  |  |  | 1 | 1 | Pump |  | Custom
[52 empty] | Chilled Water Distribution Pump |  |  | x |  |  | 1 | 1 | Pump |  | Custom
[52 empty] | Chilled Water Pump |  |  |  | x |  | 0.58 | 0.401 | Pump |  | Prescriptive
[52 empty] | CHW Pump |  |  |  |  | x | 1 | 1 | Pump |  | Custom
[52 empty] | Condenser Water Pump |  |  |  |  | x | 1 | 1 | Pump |  | Custom
[52 empty] | Heating Hot Water Pump |  |  |  |  | x | 1 | 1 | Pump |  | Custom
[52 empty] | Hot Water Pump |  |  |  | x |  | 0.646 | 0 | Pump |  | Prescriptive
[52 empty] | WS Heat Pump Circ Loop | x |  |  |  |  | 1 | 1 | Pump |  | Custom
[52 empty] | HVAC Heating Pump |  |  | x |  |  | 1 | 1 | Pump |  | Custom
[52 empty] | Process Pump | x |  | x |  |  | 1 | 1 | Pump |  | Custom
[52 empty] | Process Cooling Pump |  |  |  |  | x | 1 | 1 | Pump |  | Custom
[52 empty] | Pool Pump |  |  | x |  |  | 1 | 1 | Pump |  | Custom
[52 empty] | Boiler Supply Pump |  |  |  |  | x | 1 | 1 | Pump |  | Custom
[52 empty] | Wastewater Pump |  |  |  |  | x | 1 | 1 | Pump |  | Custom
[52 empty] | Boiler Feedwater Pump |  |  |  |  | x | 1 | 1 | Pump |  | Custom
[52 empty] | Other Pump |  |  | x |  |  | 1 | 1 | Pump |  | Custom
[52 empty] | Process Machinery | x |  |  |  |  | 1 | 1 | Pump |  | Custom
[52 empty] | Process Other | x |  |  |  |  | 1 | 1 | Pump |  | Custom
[52 empty] | Small Business Bonus | 30%
[52 empty] | Multiple Project Bonus | 10%
UtilityName
Pepco
Delmarva Power
Values from original TRC Measures sheet
[52 empty] | Net to Gross Ratio | 0.8
[52 empty] | Program Costs Percentage | 49%
[52 empty] | VFD EUL | 15
[52 empty] | Percent SP (Summer Peak) | Percent SOP (Summer Off Peak) | Percent NSP (Non Summer Peak) | Percent NSOP (Non Summer Off Peak) | Total Percent
[52 empty] | 23% | 10% | 46% | 21% | 100%
Includes measures that failed B/C test
Total Custom kW
Total Custom kWh
Note: These calculations are here so as not to create circular references to remove failed measures from totals.
[52 empty] | Average_Cost_Electricity | 0.14 | /kWh
[52 empty] | Minimum_Payback_Period | 1.5 | years
Improve Motor Efficiencies
Trade Ally Cost Override?
Note on BJ117: 7 AM - 11 PM weekdays (except holidays), June through September
Note on BK117: All other hours during June through September
Note on BL117: 7 AM - 11 PM weekdays (except holidays), October through May
Note on BM117: All other hours during October through May

## R2 WaterHeat
Water Heater Replacement Opportunities |  |  |  |  | Sect. 2c
Company Name | [5 empty] | Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
Retrofit Description | [7 empty] | FALSE | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure. (Indicated by *). Cost entered should be TOTAL cost for the measure.
Heat-Pump Water Heater – Heat-pump water heaters use half the electricity to provide the same amount of hot water each month than you currently use. The units are cost-effective for buildings where large volumes of hot water are used, such as restaurants, cafeterias, medical clinics, nursing homes, apartments with central hot water, fitness centers and gyms that have shower facilities, and many types of manufacturing plants. An incentive is available for qualifying equipment.
WATER HEATER CALCULATIONS - Enter Measure Type, Number of Units and Capacity (Gallons) Here. Report page will autofill. Hide unused lines.
Tank-Type Water Heater -- Consider replacing your existing electric water heater(s) with a new, highly efficient unit(s). An incentive is available for qualifying equipment.
Recommendation | [8 empty] | Replacement Energy Efficient Electric Water Heater
Building Information
Replace the following units with Energy Star qualified or high efficiency units. | [6 empty] | Line |  | Measure type (use drop down menu) | Number of Units | Water Heater Capacity (Gallons) | Type of Building | Average Gallons of Hot Water Use per Day | Avg. Diference between Temp. of Hot Water Produced and Cold Water Input (°F) | kBtu_req | Incentive | kWh |  | Installation Cost |  |  |  | Size | Tank | Pump
Measure | Capacity (Gal) | Qty | Energy savings (kWh) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive | Totals | [8 empty] | 0 | 0 | [5 empty] | <30 | 250 | 750 | 0
|  | 0 |  |  |  |  | 1 |  |  | 0 |  |  |  | 70 | [8 empty] | 30-40 | 500 | 750
|  | 0 |  |  |  |  | 2 |  |  | 0 |  |  |  | 70 | [8 empty] | 40-50 | 1250 | 1700
0 | 0 | 0 |  |  |  |  | 3 | [6 empty] | 70 | [8 empty] | 50+ | 1850 | 1850
0 | 0 | 0 |  |  |  |  | 4 | [6 empty] | 70
0 | 0 | 0 |  |  |  |  | 5 | [6 empty] | 70
0 | 0 | 0 |  |  |  |  | 6 | [6 empty] | 70
0 | 0 | 0 |  |  |  |  | 7 | [6 empty] | 70
0 | 0 | 0 |  |  |  |  | 8 | [6 empty] | 70
0 | 0 | 0 |  |  |  |  | 9 | [6 empty] | 70
0 | 0 | 0 |  |  |  |  | 10 | [6 empty] | 70
Total |  | 0 | 0 | 0 | 0 | 0
[18 empty] | Type of building | Consumption per occupant |  | Peak demand per occupant |  | Storage per occupant |  |  |  |  | Business Type Specific | Gallons Per Storage Capacity
[19 empty] | gal/day |  | gal/hr |  | gal |  | Gallons per storage capacity |  |  | Farms | 7.5
[18 empty] | Factories (no process) | 7.5 |  | 2 |  | 1 |  | 7.5 |  |  | Dairies | 7.5
[18 empty] | Hospitals, general | 35 |  | 7 |  | 6 |  | 6 |  |  | Livestock farm | 7.5
[18 empty] | Hospitals, mental | 25 |  | 5 |  | 6 |  | 4 |  |  | Greenhouse | 7.5
[18 empty] | Hostels | 20 |  | 10 |  | 7 |  | 3 |  |  | Refrigerated Warehouse | 5
[18 empty] | Hotels | 27.5 |  | 10 |  | 7 |  | 4 |  |  | Food Processor | 7.5
[18 empty] | Houses and flats | 27.5 |  | 10 |  | 7 |  | 4 |  |  | Fabrication | 7.5
[18 empty] | Offices | 5 |  | 2 |  | 1 |  | 5 |  |  | Process | 7.5
[18 empty] | Schools, boarding | 25 |  | 4 |  | 5 |  | 5 |  |  | Heavy manufacturing | 7.5
[18 empty] | Schools, day | 3 |  | 2 |  | 1 |  | 3 |  |  | Warehouse | 5
[28 empty] | Laboratories | 6
[18 empty] | Measure | Incentive | Type |  |  | Measure Code | Domestic Water Equipment | Incentive | Unit | EUL (Years) | Biotech | 6
[18 empty] | Electric Tank-Type Water Heater | 800 | T |  | Choice_TankType | E-W-HP-100-12 | Commercial Heat Pump Water Heater | 1500 | Unit | 10 | Office building | 5
[18 empty] | Heat Pump Water Heater | 1500 | H |  | Choice_HeatPump | E-W-TT-100-12 | Commercial Water Heater | 800 | Unit | 12 | General retail | 5
[23 empty] | E-W-XX-200-13 | [Reserved for possible future use] |  |  |  | Big box retail | 5
[18 empty] | Density of Water (lb/gallon) | 8.33 | [8 empty] | Large grocery store chain | 7.5
[18 empty] | specific heat of water (Btu/lb - °F) | 1 | [8 empty] | Warehouse | 5
[18 empty] | Days per Year | 365 | [8 empty] | Convenience store | 5
[18 empty] | kBtu to kWh conversion factor | 3.413 | [8 empty] | Hospitality/Lodging | 4
[18 empty] | EFee | 2 | [8 empty] | Assisted Living | 4
[18 empty] | EFbase | 0.904 | [8 empty] | Data Center | 5
[18 empty] | CF office | 0.63 | [8 empty] | Multifamily | 4
[18 empty] | CF school | 0.58 | [8 empty] | Grocery Stores | 5
[28 empty] | Convenience Stores | 5
[18 empty] | Choose_Building | [9 empty] | Restaurants | 7.5
[18 empty] | Office | [9 empty] | Food Services | 7.5
[18 empty] | School | [9 empty] | Car dealerships | 5
[18 empty] | Other | [9 empty] | Small retail | 5
[28 empty] | Small office | 5
[28 empty] | Multifamily | 4
[28 empty] | Federal | 5
[28 empty] | State | 5
[28 empty] | County | 5
[28 empty] | Municipality | 5
[28 empty] | Hospitals | 6
[28 empty] | Ambulatory health care | 6
[28 empty] | Nursing or residential care | 4
[28 empty] | Schools | 3
[28 empty] | College or University | 5
[28 empty] | Large Non-Profit | 5
[28 empty] | Small Non-Profit | 5
[28 empty] | Large Faith-Based | 5
[28 empty] | Small Faith-Based | 5
5
Energy Star®
Trade Ally Cost Override?

## R2 Vending
Specialized Controls Opportunities | [5 empty] | Sect. 2c
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
[8 empty] | Enter number of refrigerated and non-refrigerated vending machines that are recommended for vending machine controls here: |  |  | FALSE
Retrofit Description
During portions of the daytime hours and many of the night and weekend hours, drink and other refrigerated display, or vending machines, run in order to chill or illuminate goods when there is no demand for products for a significant amount of time. This waste represents a savings opportunity. Controllers are available that incorporate a timer, an occupancy sensor, and a current sensor to optimally manage vending machine run time. Case studies consistently show savings of 30 to 50 percent. The savings and performance of these controls have been so impressive that some states require manufacturers to provide these controls on all new beverage vending machines.
Savings Analysis
[8 empty] | Non-Refrigerated: |  | 0
[8 empty] | Refrigerated: |  | 0
|  | Number |  | Energy
| VENDING MACHINES | [6 empty] | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure. Cost entered should be TOTAL cost for the measure.
| Non-Refrigerated | 0 |  | 0 | kWh
| Refrigerated | 0 |  | 0 | kWh
| CONTROLLERS |  |  | Proposed
| Non-Refrigerated - Quantity |  |  | 0
| Controller energy savings |  |  | 0 | kWh
| Utility Estimated Replacement Cost |  |  | 70 | /unit |  |  |  | Enter Non-Refrigerated Controller Install Cost
| Replacement time, including ordering and calibration |  |  | 0 | minutes
| Refrigerated - Quantity |  |  | 0
| Controller energy savings |  |  | 0 | kWh
| Utility Estimated Replacement Cost |  |  | 140 | /unit |  |  |  | Enter Refrigerated Controller Install Cost
| Replacement time, including ordering and calibration |  |  | 0 | minutes
|  | Existing |  | Proposed | Savings
POWER AND ENERGY
| Machine energy | 0 | kWh | 0 | 0 | kWh
ANNUAL OPERATING SAVINGS
Total power cost:
| Electric energy cost: | 0 |  | 0 | 0
| Total operating cost: | 0 |  | 0 | 0 | Savings
IMPLEMENTATION COST
| Total Cost: |  |  |  | 0
| PEPCO Incentive: |  |  |  | 0
| Net cost: |  |  |  | 0
This analysis excludes O&M savings due to reduced compressor, fan, & lamp operation.
The implementation cost and rates assume the project is completed by facilities staff.
According to the vendor, existing energy use is accurate for most machines within +/- 5% with
95% confidence.
ASSUMPTIONS
|  | Demand Cost (D$): |  |  | 0 | /kW-mo
|  | Energy Cost (E$): |  |  | 0.15 | /kWh
|  | Heating hours/year: |  |  | 1000 | hr/yr
|  | Heating efficiency |  |  | 80%
|  | Heating cost: |  |  | 0 | /therm
|  | Cooling hours/year: |  |  | 4000 | hr/yr
|  | Months cooling during peak demand: |  |  | 9
|  | Cooling efficiency |  |  | 3 | COP
|  | Deemed Savings per non-refrig |  |  | 328 | kWh/yr
|  | Deemed Savings per refrig |  |  | 1485 | kWh/yr
|  | Percent units in fully conditioned space |  |  | 100%
|  | Labor Cost ($/H): |  |  | 45 | /hour
|  | PEPCO Incentive NonFridge |  |  | 60 | per/controller
|  | PEPCO Incentive Fridge |  |  | 120 | per/controller
|  | SIMPLE PAYBACK |  |  | #DIV/0! | years
Refrigerated Beverage Display Controller
Vending Machines
Trade Ally Cost Override?

## R2 Controls
Specialized Controls Opportunities |  |  |  |  | Sect. 2c
Company Name | [5 empty] | Copyright © 2012 Potomac Electric Power Company
[6 empty] | All Rights Reserved | To enter your own cost information check the box below and fill in costs where prompted. Note: If you override costs you must enter cost information for EVERY line that has a measure recommended. Cost entered should be TOTAL cost for the measure.
Smart Power Strips and Personal Occupancy Sensors | [12 empty] | FALSE
Smart Power Strips turn off accessories when a main piece of equipment such as a PC CPU is shut down. Plug Load sensors can be used to turn off unnecessary equipment when an area is unoccupied for a significant amount of time. Computer monitors, task lighting, personal fans or heaters, printers and other office equipment will all be shut down. Computer hard drives and CPUs will be left running and should be put into low power mode using energy management software.
Enter number of each control type recommended below. Enter location for office controls
Measure | Load to be Controlled | Qty | Energy savings (kWh) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive | Load/Location | Number Recommended | Control Equipment | Incentive | Unit | EUL (Yr)
"Smart" Power Strips | 0 | 0 | 0 | 0 | 0 | 0 |  |  | "Smart" Power Strips | 18 | Strip
Personal Occupancy Sensors |  | 0 | 0 | 0 | 0 | 0 |  | 0 | Personal Occupancy Sensors | 50 | Control | 10
10
Total |  | 0 | 0 | 0 | 0 | 0 | Hotel HVAC |  | Hotel Room HVAC Controls | 400 | Room | 10
[7 empty] | Hotel HVAC & Plugs |  | Hotel Room HVAC and Receptacle Controls | 450 | Room | 10
Hotel Room Occupancy Sensors
Hotels can save significant energy - up to 35% annually - by making sure guest rooms are only cooled and lit when occupied. HVAC controls can be installed on a window unit or the blower for a central system. A more comprehensive level of control also turns off equipment plugged into electrical outlets, such as lights and device chargers. The two major types of occupancy controls are cardkey systems and occupancy sensor systems.
With a cardkey system the guests are directed to place their key in a special receptacle once they have entered a room. The key receptacle acts as a master switch for the room and enables lights and the HVAC system.
With the occupancy sensor system, a door contact switch initiates the system and the occupancy sensor determines if a person is in the room. If the occupancy sensor detects the presence of a guest, it activates the HVAC system and permits guests to turn all other electrical systems on or off. The occupancy sensor does not scan the room again until the door contact is once again activated, at which time the occupancy sensor detects if the room is empty or occupied. If empty, the HVAC system and other electrical systems are deactivated.
Measure |  | Qty | Energy savings (kWh) | Energy cost savings | Utility Estimated Cost | PEPCO Incentive
Hotel Room HVAC Controls |  | 0 | 0 | 0 | 0 | 0
Hotel Room HVAC and Receptacle Controls |  | 0 | 0 | 0 | 0 | 0
Total |  | 0 | 0 | 0 | 0 | 0
Office & Hotel
Trade Ally Cost Override?

## R2 Custom (hidden)
Custom and Alternative Measure Opportunities | [5 empty] | Sect. 2c
Company Name | [5 empty] | Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
Insert Specific Measure Description here |  |  | Insert picture here (optional)
Notes: Fill in descriptions and energy saving at left. Attach additional documentation (including calculations) as needed
Measure Type | Location/Equipment Affected |  | Energy savings (kWh) | Energy cost savings | Trade Ally Proposed Cost | PEPCO Incentive
|  |  |  | 0 |  | 0
|  |  |  | 0 |  | 0
|  |  |  | 0 |  | 0
Insert Specific Measure Description here |  |  | Insert picture here (optional)
Measure Type | Location/Equipment Affected |  | Energy savings (kWh) | Energy cost savings | Trade Ally Proposed Cost | PEPCO Incentive
|  |  |  | 0 |  | 0
|  |  |  | 0 |  | 0
|  |  |  | 0 |  | 0
Insert Specific Measure Description here |  |  | Insert picture here (optional)
Measure Type | Location/Equipment Affected |  | Energy savings (kWh) | Energy cost savings | Trade Ally Proposed Cost | PEPCO Incentive
|  |  |  | 0 |  | 0
|  |  |  | 0 |  | 0 | Measure Type | Measure Code | Notes
|  |  |  | 0 |  | 0 | Lighting & Controls | C-L-OO-540-12 | All that are not prescriptive
[7 empty] | Building Controls | C-B-OO-550-12 | All EMS and BAC
[7 empty] | Chiller | C-C-OO-550-12 | Multiple or >1,000 tons
Total |  | 0 | 0 | 0 | 0 | 0 | VFD | C-V-HV-540-12 | Non-HVAC Pump or Fan
[7 empty] | HVAC | C-H-OO-550-12 | All that are not prescriptive
[7 empty] | Refrigeration | C-R-OO-550-12 | All that are not prescriptive
[7 empty] | Fluid Flow | C-F-OO-550-12 | Pump, fan, piping, duct changes
[7 empty] | Thermal insulation | C-I-OO-550-12 | All
[7 empty] | Windows | C-G-OO-550-12 | All
[7 empty] | Process Improvement | C-P-OO-550-12 | All
[7 empty] | Compressed Air | C-A-OO-550-12 | All
[7 empty] | Water Heating | C-W-OO-550-12
[7 empty] | Other | C-O-OO-550-12 | Everything else

## R3 Facil desc
| Facility Description | Sect. 3
Copyright © 2012 Potomac Electric Power Company
All Rights Reserved
Facility
Describe who or what the business is, describe what they do in this facility, describe different functions in the facility (e.g. small office with large distribution warehouse) generally describe the facility (e.g. tenant space in strip mall, two story stand alone building with sprandrel glass, tenant space in business park), estimate of the age of the facility, estimate of the size, and anything else worth noting. |  |  |  | Instructions: Replace descriptions at left with your own observations about the space. Expand row height as needed.
Equipment and Operational Characteristics
Occupancy
There are employees working here. Max Occupancy: The operating hours are:
HVAC
The HVAC consists of type of system or unit, areas served, type of heat, type of thermostat or control for hvac unit, number of units, age of units, time schedule.
Lighting
Area and task lighting is primarily XXX lighting. Describe: lighting types, fixture types, control types…
Other
Other energy uses in the building include… (kitchen equipment, motors, office equipment, etc…)
Changes over the last 12 months
List any operational, personnel, equipment, production, or any other changes that have happened over the last year. If none, report as "No changes were reported."

## W Light Exist
Existing Lighting Worksheet | [14 empty] | ENTER CHANGES TO LIGHTING HOURS IN THIS TABLE
ENTER ONLY LIGHTING YOU PLAN TO SUGGEST AN UPGRADE FOR. LIGHTING THAT IS ALREADY EFFICIENT DOES NOT NEED TO BE ENTERED HERE. | [15 empty] | Lighting |  | Lighting | Occupancy Schedule |  | Shutdowns
Select lighting type from pulldown. Enter quantity, occupancy schedule, and location. | [14 empty] | Occupancy Type | Operat- | Occupied | On-time | Weeks | Weekends | & Holidays | Weekday Schedule |  |  | Weekend Schedule
| Fixtures | [14 empty] | ing Hrs | Hrs | Factor | per year | per year | per year | Start | Stop | Hrs | Start | Stop | # days | Hrs
[11 empty] | Recommend Sensor? |  |  | A | Office | 0 | 0 | 120% | 52 | 48 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 0 | 0
|  | Total | Fixt. |  | Watts/ | Total | Occupancy | [6 empty] | B | Retail | 4939.2 | 4116 | 120% | 52 | 48 | 5 | 10:00 | 22:00 | 12 | 10:00 | 21:00 | 2 | 11
Fixture Type & Description |  | qty. | type* | Est. | fixture | kW | schedule | Hr/yr | kWh/yr | Location |  |  | Notes | C | Task lighting | 1965.6 | 3024 | 65% | 52 | 6 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4 |  |  | didn’t make it | made it
Incandescent lighting | [13 empty] | D | Daylighting | 2872.8 | 3192 | 90% | 52 | 48 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4 |  |  |  | Incandescent lighting
[14 empty] | E | Occup Sens | 2713.2 | 3192 | 85% | 52 | 48 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4
[14 empty] | F | Continuous | 8760 | 8760 | 100% | 52 | 52.5 | 0 |  |  | 24 |  |  | 2 | 24
[14 empty] | G | Common | 4149.6 | 3192 | 130% | 52 | 48 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4
[14 empty] | H | Restroom | 1596 | 3192 | 50% | 52 | 48 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4
[14 empty] | I | Exterior | 3997.9333 | 3997.9333 | 100% | 52 | 52 |  | 20:00 | 7:00 | 10.9833 | 20:00 | 7:00 | 2 | 10.9833 | 24:00 | 0:01
e
e
e
e
Compact fluorescents | [31 empty] | Compact fluorescents
e
e
e
e
e
Linear fluorescent lamps and fixtures | [31 empty] | Linear fluorescent lamps and fixtures
e
e
e
e
e
e
e
e
e
e
Exit Signs | [31 empty] | Exit Signs
F
F
F
|  |  |  | e |  |  | F
|  |  |  | e |  |  | F
|  |  |  | e |  |  | F
|  |  |  | e |  |  | F
|  |  |  | e |  |  | F
|  |  |  | e |  |  | F
|  |  |  | e |  |  | F
High intensity discharge fixtures | [31 empty] | High intensity discharge fixtures
e
e
e
e
e
Traffic Signals | [31 empty] | Traffic Signals
e
e
e
e
e
e
e
e
Exterior Parking Garage, Gasoline Canopy,Pole Lighting, Area Fixtures, & Wall Packs | [31 empty] | Exterior Parking Garage, Gasoline Canopy,Pole Lighting, Area Fixtures, & Wall Packs
e
e
e
e
e
e
e
Reach-in Freezer or Cooler Lighting | [31 empty] | Reach-in Freezer or Cooler Lighting
e
e
e
e
e
e
e
Miscellaneous
e
e
e
e
e
e
[11 empty] | 0 | kWh-exterior
[11 empty] | 0 | installed power-exterior
Notes:
Rebalance Factor
1
The below table is shown on the lighting inventory page. The on-time factor is adjusted by the rebalance factor.
[16 empty] | Lighting |  | Lighting | Occupancy Schedule |  | Shutdowns
[16 empty] | Operat- | Occupied | On-time | Weeks | Weekends | & Holidays | Weekday Schedule |  |  | Weekend Schedule
[15 empty] | Occupancy | ing Hrs | Hrs | Factor | per year | per year | per year | Start | Stop | Hrs | Start | Stop | # days | Hrs
[14 empty] | A | Office | 0 | 0 | 120% | 52 | 48 | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 0 | 0
[14 empty] | B | Retail | 4939.2 | 4116 | 120% | 52 | 48 | 5 | 10:00 | 22:00 | 12 | 10:00 | 21:00 | 2 | 11
[14 empty] | C | Task lighting | 1965.6 | 3024 | 65% | 52 | 6 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4
[14 empty] | D | Daylighting | 2872.8 | 3192 | 90% | 52 | 48 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4
[14 empty] | E | Occup Sens | 2713.2 | 3192 | 85% | 52 | 48 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4
[14 empty] | F | Continuous | 8760 | 8760 | 100% | 52 | 52.5 | 0 | 0:00 | 0:00 | 24 | 0:00 | 0:00 | 2 | 24
[14 empty] | G | Common | 4149.6 | 3192 | 130% | 52 | 48 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4
[14 empty] | H | Restroom | 1596 | 3192 | 50% | 52 | 48 | 10 | 6:00 | 18:00 | 12 | 8:00 | 12:00 | 1 | 4
[14 empty] | I | Exterior | 3997.9333 | 3997.9333 | 100% | 52 | 52 | 0 | 20:00 | 7:00 | 10.9833 | 20:00 | 7:00 | 2 | 10.9833
Validation table for light inventory, pg 2:
Yes
No

## W light ECM select
Lighting Retrofit Worksheet
[5 empty] | Name | [9 empty] | Phone Number | [13 empty] | Rebate calc
Sensor Recommendation will apply to Old fixture if no retrofit is selected and New fixture if a retrofit is selected
| Location | Sensor Recommend? | Sensor Counter | Sensor Flag | Existing Fixture - will populate from data entered on "W Light Exist" tab. | CFL/LED/T5T8/Misc | CFL counter | CFL Flag | LED Counter | LED Flag | T5T8 Counter | T5T8 Flag | Misc Counter | Misc Flag | Select Energy Efficient Retrofit Using Dropdown for Lines that have existing lighting entered | Retrofit Fixture (will populate automatically once retrofit is selected at left) | Quantity | kW exist | kW ret | hours | kWh exist | kWh ret | kWh savings | Non-coincident peak kW reduction |  | Energy Cost Savings | Simple payback | cost to retrofit | # fixtures | # lamps per fixture | total lamps | Incentive per fixture | Incentive for delamp | Total Incentive |  |  | Description | Existing | Retrofit | Location | Room Type | Op Sched
Incandescent lighting | [14 empty] | Select CFL replacement of <150W incandescent ONLY if recommending full fixture replacement!! For smaller CFL bulbs use the No-Cost/Low-Cost measure and the cost will be covered 100%! | [20 empty] | Incandescent lighting
1 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 | ledfix2 | 1
2 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 2
3 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 3
4 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 4
5 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 5
6 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 6
7 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 7
8 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 8
9 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 9
10 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 | ledfix3 | 10
11 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 11
12 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 12
13 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 13
14 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 | ledfix4 | 14
15 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 15
16 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 | ledfix4 | 16
17 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 17
18 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 18
19 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 19
20 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 20
21 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 21
22 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 22
23 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 23
24 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 24
Compact fluorescents |  |  | 0 | 0 |  | CFL/LED/T5T8/Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [25 empty] | Compact fluorescents
25 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 25
26 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 26
27 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 27
28 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 28
29 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 29
30 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 30
31 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 31
32 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 32
33 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 33
34 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 34
35 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 35
36 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 36
37 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 37
38 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 38
39 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 39
40 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 40
41 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 41
42 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 42
43 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 43
44 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 44
45 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 45
46 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 46
47 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 47
48 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 48
Linear fluorescent lamps and fixtures |  |  | 0 | 0 |  | CFL/LED/T5T8/Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [20 empty] | linfluo2 | Linear fluorescent lamps and fixtures |  |  |  | Linear fluorescent lamps and fixtures
49 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 49
50 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 50
51 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 51
52 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 52
53 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 53
54 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 54
55 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 55
56 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 56
57 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 57
58 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 58
59 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 59
60 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 60
61 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 61
62 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 62
63 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 63
64 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 64
65 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 65
66 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 66
67 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 67
68 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 68
69 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 69
70 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 70
71 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 71
72 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 72
Exit Signs |  |  | 0 | 0 |  | CFL/LED/T5T8/Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [21 empty] | Exit Signs
73 |  | No | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 73 | [5 empty] | F
74 | 0 | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 74 | 0 | 0 |  | 0 |  | F
75 | 0 | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 75 | 0 | 0 |  | 0 |  | F
76 | 0 | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 76 | 0 | 0 |  | 0 |  | F
77 | 0 | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 77 | 0 | 0 |  | 0 |  | F
78 | 0 | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 78 | 0 | 0 |  | 0 |  | F
79 | 0 | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 79 | 0 | 0 |  | 0 |  | F
80 | 0 | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 80 | 0 | 0 |  | 0 |  | F
81 | 0 | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 81 | 0 | 0 |  | 0 |  | F
82 | 0 | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 82 | 0 | 0 |  | 0 |  | F
High intensity discharge fixtures |  |  | 0 | 0 |  | CFL/LED/T5T8/Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [20 empty] | otherlight2 | High intensity discharge fixtures
83 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 83
84 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 84
85 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 85
86 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 86
87 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 87
88 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 88
89 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 89
90 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 90
91 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 91
92 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 92
93 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 93
94 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 94
95 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 95
96 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 96
97 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 97
98 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 98
99 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 99
100 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 100
101 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 101
102 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 102
103 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 103
104 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 104
105 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 105
106 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 |  | 0 |  | 106
Traffic Signals | 0 |  | 0 | 0 |  | CFL/LED/T5T8/Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [21 empty] | Traffic Signals
56 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 56 | 0 | 0 |  | 0 |  | 0
57 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 57 | 0 | 0 |  | 0 |  | 0
58 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 58 | 0 | 0 |  | 0 |  | 0
59 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 59 | 0 | 0 |  | 0 |  | 0
60 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 60 | 0 | 0 |  | 0 |  | 0
61 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 61 | 0 | 0 |  | 0 |  | 0
62 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 62 | 0 | 0 |  | 0 |  | 0
63 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 63 | 0 | 0 |  | 0 |  | 0
64 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 64 | 0 | 0 |  | 0 |  | 0
65 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 65 | 0 | 0 |  | 0 |  | 0
High intensity discharge fixtures |  |  | 0 | 0 |  | CFL/LED/T5T8/Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [21 empty] | Exterior Parking Garage, Gasoline Canopy,Pole Lighting, Area Fixtures, & Wall Packs
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 66 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 67 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 68 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 69 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 70 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 71 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 72 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 73 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 74 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 75 | 0 | 0 |  | 0 |  | 0
Reach-in Freezer or Cooler Lighting |  |  | 0 | 0 |  | CFL/LED/T5T8/Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [21 empty] | Reach-in Freezer or Cooler Lighting
107 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 107 | 0 | 0 |  | 0 |  | 0
108 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 108 | 0 | 0 |  | 0 |  | 0
109 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 109 | 0 | 0 |  | 0 |  | 0
110 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 110 | 0 | 0 |  | 0 |  | 0
111 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 111 | 0 | 0 |  | 0 |  | 0
112 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 112 | 0 | 0 |  | 0 |  | 0
113 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 113 | 0 | 0 |  | 0 |  | 0
114 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 114 | 0 | 0 |  | 0 |  | 0
115 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 115 | 0 | 0 |  | 0 |  | 0
116 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 116 | 0 | 0 |  | 0 |  | 0
Miscellaneous |  |  | 0 | 0 |  | CFL/LED/T5T8/Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [21 empty] | Miscellaneous
86 | #REF! |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 86 | 0 | 0 |  | 0 |  | 0
87 | #REF! |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 87 | 0 | 0 |  | 0 |  | 0
88 | #REF! |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 88 | 0 | 0 |  | 0 |  | 0
89 | #REF! |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 89 | 0 | 0 |  | 0 |  | 0
90 | #REF! |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 90 | 0 | 0 |  | 0 |  | 0
91 | #REF! |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 91 | 0 | 0 |  | 0 |  | 0
92 | #REF! |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 92 | 0 | 0 |  | 0 |  | 0
93 | #REF! |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 93 | 0 | 0 |  | 0 |  | 0
94 | #REF! |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | [11 empty] | 0 |  | 0 | 0 |  | 0 |  | 94 | 0 | 0 |  | 0 |  | 0
95 | #REF! |  | 0 | 0 | #REF! |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! |  | 0 | 0 |  | #REF! |  | 95 | 0 | #REF! |  | #REF! |  | #REF!
[21 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  |  | Lighting Incentive | 0
[5 empty] | Date of Survey: | [17 empty] | Coincident peak kW factor | 80%
[5 empty] | Energy Engineer: | [17 empty] | actual peak kW reduction | 0
Calculation to Determine kW cost savings(applicible only to CB-1,3 accts)
Theory: all lighting is not on at the same time and does not always contribute 100% to peak demand for month
However ratchet clause increase the kW reduction savings by lowering the billing kW in all months
[17 empty] | Month | Demand reduction each mth | kw reduction | kw $ savings | w/ ratchet clause | full kw reduction each mth
[17 empty] | Jan | 100% | 100 | 0 | 0 | 0
[17 empty] | Feb | 90% | 90 | 0 | 0 | 0
[17 empty] | Mar | 88% | 88 | 0 | 0 | 0
[17 empty] | Apr | 80% | 80 | 0 | 0 | 0
[17 empty] | May | 75% | 75 | 0 | 0 | 0
[17 empty] | Jun | 75% | 75 | 0 | 0 | 0
[17 empty] | Jul | 70% | 70 | 0 | 0 | 0
[17 empty] | Aug | 70% | 70 | 0 | 0 | 0
[17 empty] | Sep | 75% | 75 | 0 | 0 | 0
[17 empty] | Oct | 85% | 85 | 0 | 0 | 0
[17 empty] | Nov | 90% | 90 | 0 | 0 | 0
[17 empty] | Dec | 100% | 100 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0
[21 empty] | savings factor for kW | 0

## W HVAC
Instructions: Use this worksheet to estimate total HVAC tonnage for the facility and then make some assumptions about how it breaks down into unit sizes. This sheet does NOT populate other sheets. If you are recommending HVAC measures you still need to enter sizes on the other pages of the tool.
HVAC Worksheet
Unit Size Calculator
Select Building type | Enter Area (sq.ft.) | Est. Capacity (tons)
Grocery, convenience store | 4000 | 8.8889 | to pick unit size, always select the next largest size (eg. 10.4 tons, select 12.5 ton unit)
Office, multistory building | 60000 | 139.5349
Retail, small | 7500 | 17.8571
Data/server room | 100 | 1.4286
Estimate guidelines
Unit size | use calculator, above | to pick unit size, always select the next largest size (eg. 10.4 tons, select 12.5 ton unit)
If unit is on roof | Unitary Air Conditioner
Gas meter at building | Heat pump | most rooftop units will be gas heat
Air system, 1-20 tons | Constant volume
Air system, 25 tons and larger | VAV
Economizer, 1-5 tons | No
Economizer, 6.5 tons & larger | Yes
Economizer, split system | No
Age of unit | same as age of bldg
Drop Down Lists for HVAC Inventory
Unit type | Heat Type | thermostat type | System Type |  | Size Units
Unitary air conditioner | Natural gas | Mechanical, no timeclock | Const. volume |  | tons
Split system | Heat pump | Mechanical w/ timeclock | VAV reheat, VFD | VFD control of supply fan | btuh
Room air conditioner | none | Programmable, electronic | VAV reheat, inlet vane | inlet vane control of supply fan | mbh
Packaged terminal AC | Electric | Programmable, mechanical | VAV reheat, fan curve | no control for supply fan | kW
Custom built | propane | Sensor-BAS control | VAV | variable air volume, cooling only or unknown type | hp
Central plant | other | n/a | Dual duct |  | boiler hp
Chiller, air cooled |  |  | Multizone |  | bhp
Chiller, water cooled |  |  | VVT | constant volume system with control dampers | 1
Ground source heat pump |  |  | CV-Clean room |  | 2
Furnace |  |  | 100% outside air |  | 3
Unit heater |  |  | HHW | heating hot water system | 4
Water source heat pump |  |  | CHW | chilled water system | 5
Unitary heat pump |  |  | CV, no duct | systems with no ductwork, contstant volume fans
Hot water boiler |  |  | 1
Steam boiler |  |  | 2
Electric resistance heater |  |  | 3
other 2 |  |  | 4
5

## Data Benchmarks (hidden)
California Energy Commission, SCE field monitored data (grocery store)
Energy Consumption per sq ft end use
kWh/sf/yr
End Use | Heating | Cooling | Ventilation | Refrig | Water Heating | Cooking | Indoor Lighting | Outdoor lighting | Office Equipment | Misc. | Air Comp. | Motors | Process | Total | [6 empty] | End Use | Heating | Cooling | Ventilation | Refrig | Water Heating | Cooking | Indoor Lighting | Outdoor lighting | Office Equipment | Misc. | Air Comp. | Motors | Process | Total
All Commercial | 0.22 | 2.04 | 1.63 | 1.83 | 0.12 | 0.57 | 3.92 | 0.8 | 0.97 | 0.8 | 0.04 | 0.57 | 0.13 | 13.64 | [6 empty] | All Commercial | 1.613% | 14.96% | 11.95% | 13.42% | 0.8798% | 4.179% | 28.74% | 5.865% | 7.111% | 5.865% | 0.2933% | 4.179% | 0.9531% | 100%
Small office | 0.2 | 2.61 | 1.29 | 0.58 | 0.25 | 0.1 | 3.83 | 0.95 | 2.19 | 0.78 | 0 | 0.22 | 0.1 | 13.1 | [6 empty] | Small office | 1.527% | 19.92% | 9.847% | 4.427% | 1.908% | 0.7634% | 29.24% | 7.252% | 16.72% | 5.954% | 0% | 1.679% | 0.7634% | 100%
Large office | 0.49 | 3.57 | 3.06 | 0.41 | 0.12 | 0.12 | 4.46 | 0.49 | 3.58 | 0.58 | 0.03 | 0.72 | 0.09 | 17.72 | [6 empty] | Large office | 2.765% | 20.15% | 17.27% | 2.314% | 0.6772% | 0.6772% | 25.17% | 2.765% | 20.2% | 3.273% | 0.1693% | 4.063% | 0.5079% | 100%
Restaurant | 0.05 | 5.76 | 3.24 | 9.87 | 0.38 | 10.38 | 6.45 | 2.02 | 0.63 | 1.13 | 0.01 | 0.27 | 0.02 | 40.21 | [6 empty] | Restaurant | 0.1243% | 14.32% | 8.058% | 24.55% | 0.945% | 25.81% | 16.04% | 5.024% | 1.567% | 2.81% | 0.02487% | 0.6715% | 0.04974% | 100%
Retail | 0.08 | 2.21 | 1.81 | 1.03 | 0.14 | 0.22 | 6.05 | 0.92 | 0.49 | 0.69 | 0.05 | 0.29 | 0.09 | 14.07 | [6 empty] | Retail | 0.5686% | 15.71% | 12.86% | 7.321% | 0.995% | 1.564% | 43% | 6.539% | 3.483% | 4.904% | 0.3554% | 2.061% | 0.6397% | 100%
Grocery Store | 0.08 | 2.88 | 2.58 | 22.42 | 0.14 | 1.85 | 8.55 | 0.95 | 0.37 | 0.95 | 0.01 | 0.18 | 0.04 | 41 | [6 empty] | Grocery Store | 0.1951% | 7.024% | 6.293% | 54.68% | 0.3415% | 4.512% | 20.85% | 2.317% | 0.9024% | 2.317% | 0.02439% | 0.439% | 0.09756% | 100%
Warehouse, refrigerated | 0.02 | 0.33 | 0.24 | 13.44 | 0.03 | 0.04 | 2.74 | 0.35 | 0.17 | 0.57 | 0.04 | 1.82 | 0.23 | 20.02 | [6 empty] | Warehouse, refrigerated | 0.0999% | 1.648% | 1.199% | 67.13% | 0.1499% | 0.1998% | 13.69% | 1.748% | 0.8492% | 2.847% | 0.1998% | 9.091% | 1.149% | 100%
Warehouse, unrefrigerated | 0.04 | 0.33 | 0.28 | 0.28 | 0.05 | 0.02 | 2.21 | 0.26 | 0.24 | 0.39 | 0.02 | 0.29 | 0.06 | 4.47 | [6 empty] | Warehouse, unrefrigerated | 0.8949% | 7.383% | 6.264% | 6.264% | 1.119% | 0.4474% | 49.44% | 5.817% | 5.369% | 8.725% | 0.4474% | 6.488% | 1.342% | 100%
School | 0.13 | 1.17 | 0.96 | 0.5 | 0.1 | 0.18 | 2.88 | 0.74 | 0.46 | 0.25 | 0 | 0.08 | 0.01 | 7.46 | [6 empty] | School | 1.743% | 15.68% | 12.87% | 6.702% | 1.34% | 2.413% | 38.61% | 9.92% | 6.166% | 3.351% | 0% | 1.072% | 0.134% | 100%
College | 0.77 | 1.91 | 2.05 | 0.46 | 0.12 | 0.27 | 3.84 | 0.91 | 0.72 | 0.49 | 0.01 | 0.58 | 0.14 | 12.27 | [6 empty] | College | 6.275% | 15.57% | 16.71% | 3.749% | 0.978% | 2.2% | 31.3% | 7.416% | 5.868% | 3.993% | 0.0815% | 4.727% | 1.141% | 100%
Health Care | 0.71 | 3.87 | 4.04 | 0.71 | 0.08 | 0.43 | 4.81 | 0.57 | 0.86 | 2.52 | 0.01 | 0.78 | 0.22 | 19.61 | [6 empty] | Health Care | 3.621% | 19.73% | 20.6% | 3.621% | 0.408% | 2.193% | 24.53% | 2.907% | 4.386% | 12.85% | 0.05099% | 3.978% | 1.122% | 100%
Hospital | 5.42 | 9.38 | 2.89 | 0.46 | 5.78 | 0.32 | 10.82 | 0.36 | 0.68 | 13.56 |  |  |  | 49.67 | [6 empty] | Hospital | 10.91% | 18.88% | 5.818% | 0.9261% | 11.64% | 0.6443% | 21.78% | 0.7248% | 1.369% | 27.3% | 0% | 0% | 0% | 100%
Hotel/Lodging | 0.42 | 2.41 | 1.79 | 0.9 | 0.03 | 0.68 | 3.5 | 0.61 | 0.17 | 1.11 | 0 | 0.48 | 0.02 | 12.12 | [6 empty] | Hotel/Lodging | 3.465% | 19.88% | 14.77% | 7.426% | 0.2475% | 5.611% | 28.88% | 5.033% | 1.403% | 9.158% | 0% | 3.96% | 0.165% | 100%
Miscellaneous | 0.09 | 1.1 | 0.86 | 0.86 | 0.13 | 0.26 | 2.61 | 1.07 | 0.35 | 1 | 0.12 | 1.08 | 0.3 | 9.83 | [6 empty] | Miscellaneous | 0.9156% | 11.19% | 8.749% | 8.749% | 1.322% | 2.645% | 26.55% | 10.89% | 3.561% | 10.17% | 1.221% | 10.99% | 3.052% | 100%
All Offices | 0.38 | 3.23 | 2.43 | 0.47 | 0.17 | 0.11 | 4.24 | 0.65 | 3.09 | 0.65 | 0.02 | 0.54 | 0.09 | 16.07 | [6 empty] | All Offices | 2.365% | 20.1% | 15.12% | 2.925% | 1.058% | 0.6845% | 26.38% | 4.045% | 19.23% | 4.045% | 0.1245% | 3.36% | 0.56% | 100%
All Warehouses | 0.03 | 0.33 | 0.28 | 2.21 | 0.04 | 0.02 | 2.29 | 0.27 | 0.23 | 0.42 | 0.02 | 0.52 | 0.08 | 6.74 | [6 empty] | All Warehouses | 0.4451% | 4.896% | 4.154% | 32.79% | 0.5935% | 0.2967% | 33.98% | 4.006% | 3.412% | 6.231% | 0.2967% | 7.715% | 1.187% | 100%
Average Calif building | 1.1171 | 3.1757 | 2.0486 | 0.86714 | 0.90714 | 0.29857 | 4.5871 | 0.63429 | 0.87143 | 2.8214 | 0.025833 | 0.57583 | 0.10833 | 16.8131 | [6 empty] | Average Calif building | 2.346% | 14.19% | 10.78% | 15.44% | 1.537% | 3.428% | 28.64% | 5.141% | 6.35% | 7.112% | 0.2056% | 4.029% | 0.804% | 100%
[22 empty] | Other | Lighting | HVAC | Total |  | Source |  | Building Type |  |  |  | Other | Lighting | HVAC | Total |  | kbtu -> kwh
Therms/sf/yr | [20 empty] | All Commercial | 36.88% | 34.6% | 28.52% | 100% |  |  |  | All Commercial |  |  |  | 0 | 0 | 0 |  |  | 0.29307
| Heating | Cooling | Water Htg | Cooking | Misc | Process | Total | [13 empty] | Small office | 32.21% | 36.49% | 31.3% | 100% |  | energy star calc |  | Small office - MD/DC |  |  |  | 3.0135 | 3.4134 | 2.9278 | 9.3548 | 9.3548 | 0.29307
All Commercial | 0.095 | 0.004 | 0.083 | 0.059 | 0.005 | 0.015 | 0.261 |  | Note: Information in the tables above (kWh/sf/yr) and to the left (Therms/sf/yr) updated on 01-29-09. (JL) Data based on information from CEC "California Commercial End-Use Survey" (March 2006) prepared by Itron. Updated information is highlighted in Blue. Non-highlighted information is from previous audit template and did not have a specific equivalent in the CEC report. | [11 empty] | Large office | 31.88% | 27.93% | 40.18% | 100% |  | energy star calc |  | Large office - MD/DC |  |  |  | 7.1018 | 6.222 | 8.9496 | 22.2734 | 22.2734 | 0.29307
Small office | 0.086 | 0 | 0.017 | 0.001 | 0 | 0.001 | 0.105 | [13 empty] | Restaurant | 56.43% | 21.06% | 22.51% | 100% |  | 2003 cbecs |  | Restaurant - US |  |  |  | 26.017 | 9.7119 | 10.377 | 46.1059 | 46.1059 | 0.29307
Large office | 0.17204 | 0.005 | 0.026 | 0.002 | 0.001 | 0.012 | 0.21804 | [13 empty] | Retail | 21.32% | 49.54% | 29.14% | 100% |  | 2003 cbecs |  | Convenience Store - US |  |  |  | 10.828 | 25.1571 | 14.7983 | 50.7834 | 50.7834 | 0.29307
Restaurant | 0.077 | 0 | 0.486 | 1.533 | 0 | 0.003 | 2.099 | [13 empty] | Grocery Store | 63.32% | 23.17% | 13.51% | 100% |  |  |  | Grocery Store |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
Retail | 0.03 | 0 | 0.008 | 0.005 | 0.003 | 0 | 0.046 | [13 empty] | Warehouse, refrigerated | 81.62% | 15.43% | 2.947% | 100% |  |  |  | Warehouse, refrigerated |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
Grocery Store | 0.09502 | 0 | 0.077 | 0.103 | 0 | 0.001 | 0.27602 | [13 empty] | Warehouse, unrefrigerated | 30.2% | 55.26% | 14.54% | 100% |  |  |  | Warehouse, unrefrigerated |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
Warehouse, refrigerated | 0.008 | 0 | 0.003 | 0 | 0 | 0 | 0.011 | [13 empty] | School | 21.18% | 48.53% | 30.29% | 100% |  |  |  | School |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
Warehouse, unrefrigerated | 0.027 | 0 | 0.003 | 0 | 0 | 0 | 0.03 | [13 empty] | College | 22.74% | 38.71% | 38.55% | 100% |  | 2003 cbecs |  | College - US |  |  |  | 5.2672 | 8.9675 | 8.9297 | 23.1643 | 23.1643 | 0.29307
School | 0.10002 | 0.001 | 0.047 | 0.011 | 0 | 0.001 | 0.16002 | [13 empty] | Health Care | 28.61% | 27.43% | 43.96% | 100% |  |  |  | Health Care |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
College | 0.19805 | 0.035 | 0.084 | 0.017 | 0.009 | 0 | 0.34305 | [13 empty] | Hospital | 41.88% | 22.51% | 35.62% | 100% |  |  |  | Hospital |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
Health Care | 0.32708 | 0.016 | 0.314 | 0.034 | 0.014 | 0.051 | 0.75608 | [13 empty] | Hotel/Lodging | 27.97% | 33.91% | 38.12% | 100% |  |  |  | Hotel/Lodging |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
Hospital | 0.23 | 0.03 | 0.31 | 0.01 | 0.3 |  | 0.88 | [13 empty] | Miscellaneous | 41.71% | 37.44% | 20.85% | 100% |  |  |  | Miscellaneous |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
Hotel/Lodging | 0.07302 | 0.001 | 0.29 | 0.044 | 0.014 | 0.003 | 0.42502 | [13 empty] | All Offices | 31.99% | 30.43% | 37.59% | 100% |  |  |  | All Offices |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
Miscellaneous | 0.07 | 0.004 | 0.093 | 0.01 | 0.01 | 0.046 | 0.233 | [13 empty] | All Warehouses | 52.52% | 37.98% | 9.496% | 100% |  |  |  | All Warehouses |  |  |  | 0 | 0 | 0 |  | 0 | 0.29307
All Offices | 0.14203 | 0.004 | 0.023 | 0.002 | 0.001 | 0.008 | 0.18003 | [13 empty] | Average Calif building | 38.9% | 33.78% | 27.32% | 100% |  | energy star calc |  | Energy Star small office - MD/DC |  |  |  | 2.2243 | 2.5194 | 2.161 | 6.9048 | 6.9048 | 0.29307
All Warehouses | 0.02401 | 0 | 0.004 | 0.002 | 0 | 0.004 | 0.03401 | [19 empty] | energy star calc |  | Energy Star large office - MD/DC |  |  |  | 5.2554 | 4.6043 | 6.6227 | 16.4823 | 16.4823 | 0.29307
Average Calif building | 0.10964 | 0.00625 | 0.11675 | 0.11456 | 0.022312 | 0.0096667 | 0.37858 | [19 empty] | DOE report |  | ASHRAE 90.1-2007 NonRes Code - MD/DC |  |  |  | 11.86 |  |  | 11.86 | 11.86 | 0.29307
[21 empty] | Tables created 03/07/12 (JL) | [7 empty] | 0 |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | 0.29307
BuildingType Energy Usage-for estimating
|  | HVAC, incl fan energy |  |  | Heating |  | Bldg total | Natural Gas Profiles
Building Type | Typical Size ft2 | Type | sf/ton | kWh/sf | Heating, btuh/sf | therms/sf | therms/sf | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | total |  | Other | Lighting | HVAC | Total
Data/server room |  | RTU-C | 70 | 40 |  | 0 | 0 | [13 empty] | All Commercial | 5.03 | 4.72 | 3.89 | 13.64
Grocery, convenience store | 2500 | RTU | 450 | 3.25 |  | 0.05 | 0.1 | 34.34% | 10.44% | 4.67% | 2.033% | 2.467% | 1.984% | 1.83% | 1.846% | 1.753% | 2.225% | 4.918% | 31.5% | 100% | Small office | 4.22 | 4.78 | 4.1 | 13.1
Grocery, supermarket | 40000 | AHCU | 580 | 4.5 |  | 0.02 | 0.2 | 34.34% | 10.44% | 4.67% | 2.033% | 2.467% | 1.984% | 1.83% | 1.846% | 1.753% | 2.225% | 4.918% | 31.5% | 100% | Large office | 5.65 | 4.95 | 7.12 | 17.72
Heat Pump-office | 5000 | RTU-HP | 480 | 4.2 |  | 0 | 0.1 | 20.57% | 13.18% | 11.09% | 8.677% | 3.416% | 2.571% | 1.077% | 1.06% | 1.094% | 4.499% | 12.85% | 19.92% | 100% | Restaurant | 22.69 | 8.47 | 9.05 | 40.21
Heat Pump-retail | 5000 | RTU-HP | 480 | 4.5 |  | 0 | 0.02 | 14.04% | 9.979% | 9.246% | 8.067% | 6.6% | 5.893% | 5.815% | 5.684% | 5.579% | 6.312% | 9.377% | 13.41% | 100% | Retail | 3 | 6.97 | 4.1 | 14.07
Hospital |  | CENT | 250 | 17.7 |  | 0.23 | 0.88 | 14.04% | 9.979% | 9.246% | 8.067% | 6.6% | 5.893% | 5.815% | 5.684% | 5.579% | 6.312% | 9.377% | 13.41% | 100% | Grocery Store | 25.96 | 9.5 | 5.54 | 41
lodging, hotel |  |  | 480 | 7.2 | 47.4 | 0.24 | 0.48 | 14.04% | 9.979% | 9.246% | 8.067% | 6.6% | 5.893% | 5.815% | 5.684% | 5.579% | 6.312% | 9.377% | 13.41% | 100% | Warehouse, refrigerated | 16.34 | 3.09 | 0.59 | 20.02
Lodging, motel | 10000 | PTHP | 350 | 6.16 | 24.4 | 0 | 0.06 | 14.04% | 9.979% | 9.246% | 8.067% | 6.6% | 5.893% | 5.815% | 5.684% | 5.579% | 6.312% | 9.377% | 13.41% | 100% | Warehouse, unrefrigerated | 1.35 | 2.47 | 0.65 | 4.47
Manufacturing | 200000 | CENT | 225 | 13.5 |  | 0.02 | 0.05 | 14.04% | 9.979% | 9.246% | 8.067% | 6.6% | 5.893% | 5.815% | 5.684% | 5.579% | 6.312% | 9.377% | 13.41% | 100% | School | 1.58 | 3.62 | 2.26 | 7.46
Office, multistory building | 60000 | VAV | 430 | 8.2 |  | 0.71 | 1.17 | 20.57% | 13.18% | 11.09% | 8.677% | 3.416% | 2.571% | 1.077% | 1.06% | 1.094% | 4.499% | 12.85% | 19.92% | 100% | College | 2.79 | 4.75 | 4.73 | 12.27
Office, small | 5000 | RTU | 480 | 3.6 | 33 | 0.15 | 0.21 | 20.57% | 13.18% | 11.09% | 8.677% | 3.416% | 2.571% | 1.077% | 1.06% | 1.094% | 4.499% | 12.85% | 19.92% | 100% | Health Care | 5.61 | 5.38 | 8.62 | 19.61
other |  |  | 450 | 8 |  | 0.05 | 0.1 | 20.57% | 13.18% | 11.09% | 8.677% | 3.416% | 2.571% | 1.077% | 1.06% | 1.094% | 4.499% | 12.85% | 19.92% | 100% | Hospital | 20.8 | 11.18 | 17.69 | 49.67
Restaurant | 2500 | RTU | 85 | 23.06 |  | 0.1 | 9.5 | 8.172% | 7.624% | 8.719% | 8.467% | 8.467% | 7.66% | 8.5% | 8.719% | 8.172% | 8.5% | 8.4% | 8.6% | 100% | Hotel/Lodging | 3.39 | 4.11 | 4.62 | 12.12
Retail | 10000 | RTU | 500 | 4.03 |  | 0.11 | 0.26 | 34.34% | 10.44% | 4.67% | 2.033% | 2.467% | 1.984% | 1.83% | 1.846% | 1.753% | 2.225% | 4.918% | 31.5% | 100% | Miscellaneous | 4.1 | 3.68 | 2.05 | 9.83
Retail, Big Box | 80000 | RTU | 530 | 2.38 | 41.1 | 0.16 | 0.26 | 34.34% | 10.44% | 4.67% | 2.033% | 2.467% | 1.984% | 1.83% | 1.846% | 1.753% | 2.225% | 4.918% | 31.5% | 100% | All Offices | 5.14 | 4.89 | 6.04 | 16.07
Retail, small | 2500 | RTU | 420 | 3.48 |  | 0.04 | 0.1 | 34.34% | 10.44% | 4.67% | 2.033% | 2.467% | 1.984% | 1.83% | 1.846% | 1.753% | 2.225% | 4.918% | 31.5% | 100% | All Warehouses | 3.54 | 2.56 | 0.64 | 6.74
Room Air Conditioner, clg only | 500 | RAC | 330 | 2.5 |  | 0 | 0 | [13 empty] | Average Calif building | 8.1994 | 5.32 | 5.1056 | 18.625
Room Air Conditioner, heat pump | 500 | RAC-HP | 330 | 3.1 |  | 0 | 0 | 14.04% | 9.979% | 9.246% | 8.067% | 6.6% | 5.893% | 5.815% | 5.684% | 5.579% | 6.312% | 9.377% | 13.41% | 100%
School, college |  | RTU | 500 | 10.7 |  | 0.37 | 0.49 | 25.2% | 13.77% | 8.171% | 7.204% | 5.86% | 3.231% | 3.655% | 5.353% | 3.667% | 4.964% | 11.64% | 7.287% | 100%
School, k-12 | 35000 | RTU | 440 | 4.12 | 45 | 0.49 | 0.66 | 25.2% | 13.77% | 8.171% | 7.204% | 5.86% | 3.231% | 3.655% | 5.353% | 3.667% | 4.964% | 11.64% | 7.287% | 100%
Warehouse, conditioned | 200000 | RTU | 600 | 1.56 | 38.2 | 0.03 | 0.038155 | 20.57% | 13.18% | 11.09% | 8.677% | 3.416% | 2.571% | 1.077% | 1.06% | 1.094% | 4.499% | 12.85% | 19.92% | 100% | DOE - Commercial building, floorspace, energy consumption, and energy intensity, by building activity
Warehouse, heating only |  | UH |  | 0.0261 |  | 0.2 |  | 20.57% | 13.18% | 11.09% | 8.677% | 3.416% | 2.571% | 1.077% | 1.06% | 1.094% | 4.499% | 12.85% | 19.92% | 100% | From 'Buildings Energy Data Book;' http://buildingsdatabook.eren.doe.gov/ChapterView.aspx?chap=3
[21 empty] | Incomplete - Work in progress | [5 empty] | Percent
|  | PTHP | Packaged Terminal Heat Pump | [20 empty] | Thousand Btu/sf | Therms/sf |  | Total Floorspace | Primary Energy Consumption
|  | RTU | Unitary rooftop unit, gas/elec. (gas heating, electric cooling) | [17 empty] | Vacant |  |  | 21 | 0.21 |  | 4% | 1%
|  | VAV | Unitary HVAC, VAV, hot water reheat | [17 empty] | Product Order and Safety |  |  | 116 | 1.16 |  | 2% | 2%
|  | RTU-HP | Unitary rooftop unit, heat pump (elec heating and elec cooling) | [17 empty] | Religious Worship |  |  | 44 | 0.44 |  | 5% | 2%
|  | VAV | Unitary HVAC, VAV, hot water reheat | [17 empty] | Other |  |  | 164 | 1.64 |  | 2% | 4%
|  | AHCU | Split system, Air handler, condensing unit, heat recovery | [17 empty] | Service |  |  | 77 | 0.77 |  | 6% | 4%
|  | PTAC | packaged terminal air conditioners | [17 empty] | Food Sales |  |  | 200 | 2 |  | 2% | 5%
|  | RTU-C | Unitary rooftop unit, cooling only | [17 empty] | Public Assembly |  |  | 94 | 0.94 |  | 6% | 5%
|  | CENT | Central plant, air handlers, Chilled water, hot water | [17 empty] | Food Service |  |  | 258 | 2.58 |  | 2% | 6%
|  | UH | space unit heater, gas heat, prop fan. | [17 empty] | Warehouse and Storage |  |  | 45 | 0.45 |  | 14% | 7%
[21 empty] | Lodging |  |  | 100 | 1 |  | 7% | 7%
[21 empty] | Health Care |  |  | 188 | 1.88 |  | 4% | 8%
[21 empty] | Education |  |  | 83 | 0.83 |  | 14% | 11%
Table 1: Changes to Lighting Power Densities Title 24 lighting standards |  |  |  | Does MD or DC have an equivalent to title 24? Need to research. | [16 empty] | Mercantile |  |  | 91 | 0.91 |  | 16% | 18%
|  | Watt per square foot allowed |  | Christa 2/16/2012 | [16 empty] | Office |  |  | 93 | 0.93 |  | 17% | 19%
Use |  | 2001 stds | 2005 stds | 2008 stds | [18 empty] | Average | 112.4286 | 1.1243 | Totals | 101% | 99%
| Auditorium | 2 | 1.5 | 1.5
| Auto repair | 1.2 | 1.1 | 0.9 | [19 empty] | Watt-hr/sf | kWh/sf
| Classrooms | 1.6 | 1.2 | 1.1 | [16 empty] | Vacant |  |  | 6155.1 | 6.1551
| Convention, conference | 1.5 | 1.4 | 1.4 | [16 empty] | Product Order and Safety |  |  | 33999.6 | 33.9996
| C&I workplaces-high bay | 1.2 | 1.1 | 1 | [16 empty] | Religious Worship |  |  | 12896.4 | 12.8964
| C&I Precision work | 1.5 | 1.3 | 1.2 | [16 empty] | Other |  |  | 48068.4 | 48.0684
| Hotel function | 2.2 | 1.5 | 1.5 | [16 empty] | Service |  |  | 22568.7 | 22.5687
| Hotel lobby | 1.7 | 1.1 | 1.1 | [16 empty] | Food Sales |  |  | 58620 | 58.62
| Food prep | 1.7 | 1.6 | 1.6 | [16 empty] | Public Assembly |  |  | 27551.4 | 27.5514
| Medical care | 1.4 | 1.2 | 1.2 | [16 empty] | Food Service |  |  | 75619.8 | 75.6198
| Office | 1.3 | 1.2 | 0.85 | [16 empty] | Warehouse and Storage |  |  | 13189.5 | 13.1895
| Religious worship | 2.1 | 1.5 | 1.5 | [16 empty] | Lodging |  |  | 29310 | 29.31
| Retail, wholesale showrooms | 2 | 1.7 | 1.6 | [16 empty] | Health Care |  |  | 55102.8 | 55.1028
Note: Above Title 24 2008 Lighting Standards entered 03/06/12 (JL) | [20 empty] | Education |  |  | 24327.3 | 24.3273
[21 empty] | Mercantile |  |  | 26672.1 | 26.6721
[21 empty] | Office |  |  | 27258.3 | 27.2583
2005 Title 24 lighting power density allowances | [5 empty] | 2008 Title 24 lighting power density allowances | [16 empty] | Average | 32952.8143 | 32.9528
Table 146-B & C of EE stds | [5 empty] | Table 146-E & F of EE stds
|  | watts/sf |  |  |  | Entered 03/06/12 (JL) |  | Natural Gas Profiles Jun: watts/sf
Type of Use |  | Whole Bldg | Area Category | Benchmark value |  | Type of Use |  | Natural Gas Profiles May: Whole Bldg; Natural Gas Profiles Jun: Area Category; Natural Gas Profiles Jul: Benchmark Value
Auditorium |  | 1.5 | 1.5 | 1.5 |  | Auditorium |  | Natural Gas Profiles May: 1.5; Natural Gas Profiles Jun: 1.5; Natural Gas Profiles Jul: 1.5
Auto repair |  |  | 1.1 | 1.1 |  | Auto repair |  | Natural Gas Profiles Jun: 0.9; Natural Gas Profiles Jul: 0.9
Classrooms, lecture, vocational, training |  |  | 1.2 | 1.2 |  | Beauty salon |  | Natural Gas Profiles Jun: 1.7; Natural Gas Profiles Jul: 1.7
Civic meeting place |  |  | 1.3 | 1.3 |  | Civic Meeting Place |  | Natural Gas Profiles Jun: 1.3; Natural Gas Profiles Jul: 1.3
Commercial and industrial storage-whole bldg |  | 0.7 |  | 0.7 |  | Classroom building |  | Natural Gas Profiles May: 1.1; Natural Gas Profiles Jul: 1.1
Commercial and industrial storage areas |  |  | 0.6 | 0.6 |  | Classrooms, lecture, training, vocational room |  | Natural Gas Profiles Jun: 1.2; Natural Gas Profiles Jul: 1.2
Convention centers-whole building |  | 1.3 |  | 1.3 |  | Commerical and industrial storage buildings |  | Natural Gas Profiles May: 0.6; Natural Gas Profiles Jul: 0.6
Convention, conference, multipurpose, meeting centers |  |  | 1.4 | 1.4 |  | Commerical and industrial storage (conditioned & unconditioned) |  | Natural Gas Profiles Jun: 0.6; Natural Gas Profiles Jul: 0.6
Corridors, restrooms, stairs, support areas |  |  | 0.6 | 0.6 |  | Commerical and industrial storage (refrigerated) |  | Natural Gas Profiles Jun: 0.7; Natural Gas Profiles Jul: 0.7
Dining area |  |  | 1.1 | 1.1 |  | Convention centers |  | Natural Gas Profiles May: 1.2; Natural Gas Profiles Jul: 1.2
Electrical, mechanical rooms |  |  | 0.7 | 0.7 |  | Convention, conferences, multipurpose and meeting centers |  | Natural Gas Profiles Jun: 1.4; Natural Gas Profiles Jul: 1.4
Exercise center, gymnasium |  |  | 1 | 1 |  | Corridors, restrooms, stairs, and support areas |  | Natural Gas Profiles Jun: 0.6; Natural Gas Profiles Jul: 0.6
Exhibit, museum |  |  | 2 | 2 |  | Dining |  | Natural Gas Profiles Jun: 1.1; Natural Gas Profiles Jul: 1.1
Financial institutions-whole building |  | 1.1 |  | 1.1 |  | Electrical, mechanical, telephone rooms |  | Natural Gas Profiles Jun: 0.7; Natural Gas Profiles Jul: 0.7
Financial transactions |  |  | 1.2 | 1.2 |  | Exercise center, gymnasium | bar: Natural Gas Profiles Jun to Natural Gas Profiles Jul
General comm & ind. work-whole building |  | 1.1 |  | 1.1 |  | Exhibit, museum |  | Natural Gas Profiles Jun: 2; Natural Gas Profiles Jul: 2
General comm & ind. work-high bay |  |  | 1.1 | 1.1 |  | Financial institutions |  | Natural Gas Profiles May: 1.1; Natural Gas Profiles Jul: 1.1
General comm & ind. work-low bay |  |  | 1 | 1 |  | Financial transactions |  | Natural Gas Profiles Jun: 1.2; Natural Gas Profiles Jul: 1.2
General comm & ind. work-precision |  |  | 1.3 | 1.3 |  | General commercial and industrial work buildings |  | Natural Gas Profiles Jul: 1.0333; Natural Gas Profiles Aug: AVG
Grocery stores-whole building |  | 1.5 |  | 1.5 |  | General comm & ind. work - low bay |  | Natural Gas Profiles May: 1; Natural Gas Profiles Jun: 0.9; Natural Gas Profiles Jul: 0.9
Grocery sales area |  |  | 1.6 | 1.6 |  | General comm & ind. work - high bay | bar: Natural Gas Profiles May to Natural Gas Profiles Jul
Housing, public & common areas, multi-family |  |  | 1 | 1 |  | General comm & ind. work - precision |  | Natural Gas Profiles Jun: 1.2; Natural Gas Profiles Jul: 1.2
Hotel-whole building |  | 1.4 |  | 1.4 |  | Grocery stores - whole building |  | Natural Gas Profiles May: 1.5; Natural Gas Profiles Jul: 1.5
Hotel function areas |  |  | 1.5 | 1.5 |  | Grocery sales area |  | Natural Gas Profiles Jun: 1.6; Natural Gas Profiles Jul: 1.6
Hotel, lobby |  |  | 1.1 | 1.1 |  | Hotel function areas |  | Natural Gas Profiles Jun: 1.5; Natural Gas Profiles Jul: 1.5
Kitchen, food preparation |  |  | 1.6 | 1.6 |  | Lobbies - Hotel |  | Natural Gas Profiles Jun: 1.1; Natural Gas Profiles Jul: 1.1
Laundry |  |  | 0.9 | 0.9 |  | Housing, Public and Commons Areas - Multi-family, Dormitory | bar: Natural Gas Profiles Jun to Natural Gas Profiles Jul
Library, reading area |  |  | 1.2 | 1.2 |  | Housing, Public and Commons Areas - Senior Housing |  | Natural Gas Profiles Jun: 1.5; Natural Gas Profiles Jul: 1.5
Library, stacks |  |  | 1.5 | 1.5 |  | Kitchen, food preparation |  | Natural Gas Profiles Jun: 1.6; Natural Gas Profiles Jul: 1.6
Lobbies |  |  | 1.5 | 1.5 |  | Laboratory, Scientific |  | Natural Gas Profiles Jun: 1.4; Natural Gas Profiles Jul: 1.4
Locker/dressing room |  |  | 0.8 | 0.8 |  | Laundry |  | Natural Gas Profiles Jun: 0.9; Natural Gas Profiles Jul: 0.9
Lounge/recreation |  |  | 1.1 | 1.1 |  | Library - whole building |  | Natural Gas Profiles May: 1.3; Natural Gas Profiles Jul: 1.3
Malls and atrias |  |  | 1.2 | 1.2 |  | Library - Reading Areas |  | Natural Gas Profiles Jun: 1.2; Natural Gas Profiles Jul: 1.2
Medical buildings and clinics |  | 1.1 |  | 1.1 |  | Library - Stacks |  | Natural Gas Profiles Jun: 1.5; Natural Gas Profiles Jul: 1.5
Medical and clinical care areas |  |  | 1.2 | 1.2 |  | Lobbies - Main entry lobby |  | Natural Gas Profiles Jun: 1.5; Natural Gas Profiles Jul: 1.5
Office building |  | 1.1 |  | 1.1 |  | Locker/dressing room |  | Natural Gas Profiles Jun: 0.8; Natural Gas Profiles Jul: 0.8
Office space |  |  | 1.2 | 1.2 |  | Lounge/recreation |  | Natural Gas Profiles Jun: 1.1; Natural Gas Profiles Jul: 1.1
Parking garage |  | 0.4 |  | 0.4 |  | Malls and atria |  | Natural Gas Profiles Jun: 1.2; Natural Gas Profiles Jul: 1.2
Religious facilities |  | 1.6 |  | 1.6 |  | Medical buildings and clinics |  | Natural Gas Profiles May: 1.1; Natural Gas Profiles Jul: 1.1
Religious, worship areas |  |  | 1.5 | 1.5 |  | Medical and clinical care areas |  | Natural Gas Profiles Jun: 1.2; Natural Gas Profiles Jul: 1.2
Retail and wholesale stores |  | 1.5 |  | 1.5 |  | Office buildings |  | Natural Gas Profiles May: 0.85; Natural Gas Profiles Jul: 0.85
Retail, mechandise sales, showrooms |  |  | 1.7 | 1.7 |  | Offices - > 250 sq ft |  | Natural Gas Profiles Jun: 0.9; Natural Gas Profiles Jul: 0.9
Schools |  | 1.2 |  | 1.2 |  | Offices - <= 250 sq ft |  | Natural Gas Profiles Jun: 1.1; Natural Gas Profiles Jul: 1.1
Tenant lease space |  |  | 1 | 1 |  | Parking garages - whole building |  | Natural Gas Profiles May: 0.3; Natural Gas Profiles Jul: 0.3
Transportation |  |  | 1.2 | 1.2 |  | Parking garage - Parking area |  | Natural Gas Profiles Jun: 0.2; Natural Gas Profiles Jul: 0.2
Theaters |  | 1.3 |  | 1.3 |  | Parking garage - Ramps and Entries |  | Natural Gas Profiles Jun: 0.6; Natural Gas Profiles Jul: 0.6
Theaters, motion picture |  |  | 0.9 | 0.9 |  | Religious facilities |  | Natural Gas Profiles May: 1.6; Natural Gas Profiles Jul: 1.6
Theaters, performance |  |  | 1.4 | 1.4 |  | Religious worship |  | Natural Gas Profiles Jun: 1.5; Natural Gas Profiles Jul: 1.5
Waiting area |  |  | 1.1 | 1.1 |  | Restaurants |  | Natural Gas Profiles May: 1.2; Natural Gas Profiles Jul: 1.2
All others |  | 0.6 | 0.6 | 0.6 |  | Retail merchandise sales, wholesale, showrooms |  | Natural Gas Profiles Jun: 1.6; Natural Gas Profiles Jul: 1.6
Schools - buildings | bar: Natural Gas Profiles May; Natural Gas Profiles Jul
Tenant lease space | bar: Natural Gas Profiles Jun to Natural Gas Profiles Jul
[6 empty] | Theaters - whole building |  | Natural Gas Profiles May: 1.3; Natural Gas Profiles Jul: 1.3
[6 empty] | Theaters - motion picture |  | Natural Gas Profiles Jun: 0.9; Natural Gas Profiles Jul: 0.9
[6 empty] | Theaters - performance |  | Natural Gas Profiles Jun: 1.4; Natural Gas Profiles Jul: 1.4
[6 empty] | Transportation Function |  | Natural Gas Profiles Jun: 1.2; Natural Gas Profiles Jul: 1.2
[6 empty] | Waiting area |  | Natural Gas Profiles Jun: 1.1; Natural Gas Profiles Jul: 1.1
[6 empty] | All others |  | Natural Gas Profiles May: 0.6; Natural Gas Profiles Jun: 0.6; Natural Gas Profiles Jul: 0.6

## Data light kwh (hidden)
Lighting Inventory Reference Data
[5 empty] | Ballast | Lamp | Total | Incentive
Fixt. Code | Fixture Description | Ballast | #Ballasts | #Lamps | Watts | Watts | Watts | Retrofit | New | Delamp | Notes
FT8 | Fluor_T8_Linear
(Existing Fixture)
Typical Linear Fluorescent Fixtures
Intentionally Blank
Typ_1 | Fluorescent, 24" T12 lamp | STD | 1 | 1 | 8 | 20 | 28
Typ_2 | Fluorescent, 24" (2) T12 lamps | STD | 2 | 2 | 8 | 20 | 56
Typ_3 | Fluorescent, 24" (3) T12 lamps | STD | 1 | 3 | 8 | 20 | 68
Typ_4 | Fluorescent, 24" (4) T12 lamps | STD | 2 | 4 | 10 | 20 | 100
Typ_5 | Fluorescent, 24" T8 lamp | Electronic | 1 | 1 | 3 | 17 | 20
Typ_6 | Fluorescent, 24" (2) T8 lamps | Electronic | 1 | 2 | 3 | 17 | 37
Typ_7 | Fluorescent, 24" (3) T8 lamps | Electronic | 1 | 3 | 3 | 17 | 54
Typ_8 | Fluorescent, 24" (4) T8 lamps | Electronic | 2 | 4 | 3 | 17 | 74
Typ_9 | Fluorescent, 48" T12 lamp | STD | 1 | 1 | 10 | 40 | 50
Typ_10 | Fluorescent, 48" (2) T12 lamps | STD | 1 | 2 | 16 | 40 | 96
Typ_11 | Fluorescent, 48" (3) T12 lamps | STD | 1.5 | 3 | 10 | 40 | 135
Typ_12 | Fluorescent, 48" (4) T12 lamps | STD | 2 | 4 | 10 | 40 | 180
Typ_13 | Fluorescent, 48" (6) T12 lamps | STD | 2 | 6 | 10 | 40 | 260
Typ_14 | Fluorescent, 48" T8 lamp | Electronic | 1 | 1 | 3 | 32 | 35
Typ_15 | Fluorescent, 48" (2) T8 lamps | Electronic | 1 | 2 | 3 | 32 | 67
Typ_16 | Fluorescent, 48" (3) T8 lamps | Electronic | 2 | 3 | 3 | 32 | 102
Typ_17 | Fluorescent, 48" (4) T8 lamps | Electronic | 2 | 4 | 3 | 32 | 134
Typ_18 | Fluorescent, 48" (6) T8 lamps | Electronic | 2 | 6 | 3 | 32 | 198
Typ_19 | Fluorescent, 96" T12 lamp | STD | 1 | 1 | 15 | 75 | 90
Typ_20 | Fluorescent, 96" (2) T12 lamps | STD | 1 | 2 | 15 | 75 | 165
Typ_21 | Fluorescent, 96" (4) T12 lamps | STD | 2 | 4 | 15 | 75 | 330
Typ_22 | Fluorescent, 96" T8 lamp | Electronic | 1 | 1 | 6 | 53 | 59
Typ_23 | Fluorescent, 96" (2) T8 lamps | Electronic | 1 | 2 | 6 | 53 | 112
Typ_24 | Fluorescent, 96" (4) T8 lamps | Electronic | 1 | 4 | 8 | 53 | 220
Typ_25 | U-Tube, (2) T12 lamps | STD | 1 | 2 | 15 | 40 | 95
Typ_26 | U-Tube, (2) T8 lamps | Electronic | 1 | 2 | 6 | 32 | 70
Intentionally Blank
Specific Linear Fluorescent Fixtures
Intentionally Blank
F1.51LS | Fluorescent, (1) 18" T-8 lamp | Mag-STD |  | 1 |  | 15 | 19 | 0 | 0 | 0
Intentionally Blank
F1.52LS | Fluorescent, (2) 18" T-8 lamps | Mag-STD |  | 2 |  | 15 | 36 | 0 | 0 | 0
Intentionally Blank
F21ILL | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 17 | 18 | 0 | 0 | 0
F21ILL/T2 | Fluorescent, (1) 24", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 17 | 16.5 | 0 | 0 | 0
F21ILL/T2-R | Fluorescent, (1) 24", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 17 | 15 | 0 | 0 | 0
F21ILL/T3 | Fluorescent, (1) 24", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 17 | 15.6667 | 0 | 0 | 0
F21ILL/T3-R | Fluorescent, (1) 24", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 17 | 13.6667 | 0 | 0 | 0
F21ILL/T4 | Fluorescent, (1) 24", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 17 | 14.75 | 0 | 0 | 0
F21ILL/T4-R | Fluorescent, (1) 24", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 17 | 13.25 | 0 | 0 | 0
F21ILL-R | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 17 | 17 | 0 | 0 | 0
F21ILU | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 17 | 17 | 0 | 0 | 0
F21ILU-R | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 17 | 15 | 0 | 0 | 0
F21ILU-V | Fluorescent, (1) 24", T-8 lamps, Instant Start Ballast, VHLO ( BF > 1.1) | Prem. Elec. |  | 1 |  | 17 | 22 | 0 | 0 | 0
F21LL | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 17 | 16 | 0 | 0 | 0
F21LL/T2 | Fluorescent, (1) 24", T-8 lamp, Tandem 2-Lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 17 | 15.5 | 0 | 0 | 0
F21LL/T3 | Fluorescent, (1) 24", T-8 lamp, Tandem 3-Lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 17 | 17.3333 | 0 | 0 | 0
F21LL/T4 | Fluorescent, (1) 24", T-8 lamp, Tandem 4-Lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 17 | 17 | 0 | 0 | 0
F21LL-R | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 17 | 15 | 0 | 0 | 0
F21SL | Fluorescent, (1) 24", T-8 lamp, Standard Ballast | Mag-STD |  | 1 |  | 17 | 24 | 0 | 0 | 0
Intentionally Blank
F22ILL | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 17 | 33 | 0 | 0 | 0
F22ILL/T4 | Fluorescent, (2) 24", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 17 | 29.5 | 0 | 0 | 0
F22ILL/T4-R | Fluorescent, (2) 24", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF<.85) | Electronic |  | 2 |  | 17 | 26.5 | 0 | 0 | 0
F22ILL-R | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 17 | 30 | 0 | 0 | 0
F22ILU | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 17 | 30 | 0 | 0 | 0
F22ILU/T4-R | Fluorescent, (2) 24", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 17 | 26 | 0 | 0 | 0
F22ILU-R | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 17 | 27 | 0 | 0 | 0
F22ILU-V | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, VHLO ( BF > 1.1) | Prem. Elec. |  | 2 |  | 17 | 41 | 0 | 0 | 0
F22LL | Fluorescent, (2) 24", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 17 | 31 | 0 | 0 | 0
F22LL/T4 | Fluorescent, (2) 24", T-8 lamps, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 17 | 34 | 0 | 0 | 0
F22LL-R | Fluorescent, (2) 24", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 17 | 28 | 0 | 0 | 0
Intentionally Blank
F23ILL | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 17 | 47 | 0 | 0 | 0
F23ILL-H | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 3 |  | 17 | 51 | 0 | 0 | 0
F23ILL-R | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 3 |  | 17 | 41 | 0 | 0 | 0
F23ILU | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 17 | 45 | 0 | 0 | 0
F23ILU-R | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 3 |  | 17 | 40 | 0 | 0 | 0
F23ILU-V | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, VHLO ( BF > 1.1) | Prem. Elec. |  | 3 |  | 17 | 59 | 0 | 0 | 0
F23LL | Fluorescent, (3) 24", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 17 | 52 | 0 | 0 | 0
F23LL-R | Fluorescent, (3) 24", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 3 |  | 17 | 41 | 0 | 0 | 0
Intentionally Blank
F24ILL | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 17 | 59 | 0 | 0 | 0
F24ILL-R | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 4 |  | 17 | 53 | 0 | 0 | 0
F24ILU | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 17 | 57 | 0 | 0 | 0
F24ILU-R | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 4 |  | 17 | 52 | 0 | 0 | 0
F24LL | Fluorescent, (4) 24", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 17 | 68 | 0 | 0 | 0
F24LL-R | Fluorescent, (4) 24", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 4 |  | 17 | 57 | 0 | 0 | 0
Intentionally Blank
F31ILL | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 26 | 0 | 0 | 0
F31ILL/T2 | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 23 | 0 | 0 | 0
F31ILL/T2-H | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp IS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 25 | 26 | 0 | 0 | 0
F31ILL/T2-R | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 25 | 21 | 0 | 0 | 0
F31ILL/T3 | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 22.6667 | 0 | 0 | 0
F31ILL/T3-R | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 25 | 20.3333 | 0 | 0 | 0
F31ILL/T4 | Fluorescent, (1) 36", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 22 | 0 | 0 | 0
F31ILL/T4-R | Fluorescent, (1) 36", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 25 | 19.5 | 0 | 0 | 0
F31ILL-H | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 25 | 28 | 0 | 0 | 0
F31ILL-R | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 25 | 22 | 0 | 0 | 0
F31ILU | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 25 | 23 | 0 | 0 | 0
F31ILU/T2 | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 25 | 22 | 0 | 0 | 0
F31ILU/T2-R | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 25 | 19.5 | 0 | 0 | 0
F31ILU/T3-R | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 25 | 19.3333 | 0 | 0 | 0
F31ILU/T4-R | Fluorescent, (1) 36", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 25 | 19.25 | 0 | 0 | 0
F31ILU-R | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 25 | 20 | 0 | 0 | 0
F31LL | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 24 | 0 | 0 | 0
F31LL/T2 | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 23 | 0 | 0 | 0
F31LL/T3 | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 24 | 0 | 0 | 0
F31LL/T4 | Fluorescent, (1) 36", T-8 lamp, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 22.25 | 0 | 0 | 0
F31LL-H | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 25 | 26 | 0 | 0 | 0
F31LL-R | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 25 | 23 | 0 | 0 | 0
Intentionally Blank
F32ILL | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 46 | 0 | 0 | 0
F32ILL/2-R | Fluorescent, (2) 36", T-8 lamps, (2) Instant Start Ballasts, RLO (BF< 0.85) | Electronic |  | 2 |  | 25 | 44 | 0 | 0 | 0
F32ILL/T4 | Fluorescent, (2) 36", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 44 | 0 | 0 | 0
F32ILL/T4-R | Fluorescent, (2) 36", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 25 | 39 | 0 | 0 | 0
F32ILL-H | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 2 |  | 25 | 52 | 0 | 0 | 0
F32ILL-R | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 25 | 42 | 0 | 0 | 0
F32ILU | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 25 | 44 | 0 | 0 | 0
F32ILU/T4-R | Fluorescent, (2) 36", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 25 | 38.5 | 0 | 0 | 0
F32ILU-R | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 25 | 39 | 0 | 0 | 0
F32LL | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 46 | 0 | 0 | 0
F32LL/T4 | Fluorescent, (2) 36", T-8 lamps, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 44.5 | 0 | 0 | 0
F32LL-H | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 2 |  | 25 | 50 | 0 | 0 | 0
F32LL-R | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 25 | 42 | 0 | 0 | 0
F32LL-V | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 25 | 70 | 0 | 0 | 0
Intentionally Blank
F33ILL | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 25 | 68 | 0 | 0 | 0
F33ILL-R | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 3 |  | 25 | 61 | 0 | 0 | 0
F33ILU | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 25 | 65 | 0 | 0 | 0
F33ILU-R | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 3 |  | 25 | 58 | 0 | 0 | 0
F33LL | Fluorescent, (3) 36", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 25 | 72 | 0 | 0 | 0
F33LL-R | Fluorescent, (3) 36", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 3 |  | 25 | 62 | 0 | 0 | 0
Intentionally Blank
F34ILL | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 25 | 88 | 0 | 0 | 0
F34ILL/2-R | Fluorescent, (4) 36", T-8 lamps, (2) Instant Start Ballasts, RLO (BF< 0.85) | Electronic |  | 4 |  | 25 | 84 | 0 | 0 | 0
F34ILL-R | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 4 |  | 25 | 78 | 0 | 0 | 0
F34ILU | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 25 | 86 | 0 | 0 | 0
F34ILU-R | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 4 |  | 25 | 77 | 0 | 0 | 0
F34LL | Fluorescent, (4) 36", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 25 | 89 | 0 | 0 | 0
F34LL-R | Fluorescent, (4) 36", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 4 |  | 25 | 84 | 0 | 0 | 0
Intentionally Blank
F36ILL/2 | Fluorescent, (6) 36", T-8 lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 6 |  | 25 | 135 | 0 | 0 | 0
F36ILL/2-R | Fluorescent, (6) 36", T-8 lamps, (2) Instant Start Ballasts, RLO (BF< 0.85) | Electronic |  | 6 |  | 25 | 121 | 0 | 0 | 0
Intentionally Blank
F41GELL | Fluorescent (1) 48" T-8 @ 30W lamp, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 1 |  | 30 | 28 | 0 | 0 | 0
F41GELL-R | Fluorescent (1) 48" T-8 @ 30W lamp, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 1 |  | 30 | 24 | 0 | 0 | 0
F41GLL | Fluorescent (1) 48" T-8 lamp, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 1 |  | 32 | 30 | 0 | 0 | 0
F41GLL-R | Fluorescent (1) 48" T-8 lamp, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 1 |  | 32 | 25 | 0 | 0 | 0
F41GNLL | Fluorescent (1) 48" T-8 @ 25W lamp, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 1 |  | 25 | 24 | 0 | 0 | 0
F41GNLL-R | Fluorescent (1) 48" T-8 @ 25W lamp, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 1 |  | 25 | 21 | 0 | 0 | 0
F41GRLL | Fluorescent (1) 48" T-8 @ 28W lamp, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 1 |  | 28 | 26 | 0 | 0 | 0
F41GRLL-R | Fluorescent (1) 48" T-8 @ 28W lamp, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 1 |  | 28 | 22 | 0 | 0 | 0
F41IELL | Fluorescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 30 | 29 | 0 | 0 | 0
F41IELL/T2 | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 30 | 27.5 | 0 | 0 | 0
F41IELL/T3 | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 30 | 27 | 0 | 0 | 0
F41IELL/T4 | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 30 | 26.5 | 0 | 0 | 0
F41IELL-H | Fluorescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 30 | 34 | 0 | 0 | 0
F41IELL-R | Fluorescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 1 |  | 30 | 26 | 0 | 0 | 0
F41IELU | Fluorescent, (1) 48", T-8 @ 30W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 30 | 27 | 0 | 0 | 0
F41IELU/T2 | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 30 | 26 | 0 | 0 | 0
F41IELU/T2-R | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 30 | 22.5 | 0 | 0 | 0
F41IELU/T3 | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 30 | 25.6667 | 0 | 0 | 0
F41IELU/T3-R | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 30 | 22.6667 | 0 | 0 | 0
F41IELU/T4 | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 30 | 25.25 | 0 | 0 | 0
F41IELU/T4-R | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 30 | 22.25 | 0 | 0 | 0
F41IELU-H | Fluorescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Prem. Elec. |  | 1 |  | 30 | 32 | 0 | 0 | 0
F41IELU-R | Fluorescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 30 | 24 | 0 | 0 | 0
F41ILL | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 31 | 0 | 0 | 0
F41ILL/T2 | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 29 | 0 | 0 | 0
F41ILL/T2-H | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 32 | 33 | 0 | 0 | 0
F41ILL/T2-R | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 25.5 | 0 | 0 | 0
F41ILL/T3 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 28.3333 | 0 | 0 | 0
F41ILL/T3-H | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 32 | 31 | 0 | 0 | 0
F41ILL/T3-R | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 25.3333 | 0 | 0 | 0
F41ILL/T4 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 28 | 0 | 0 | 0
F41ILL/T4-R | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 24.5 | 0 | 0 | 0
F41ILL-H | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 32 | 36 | 0 | 0 | 0
F41ILL-R | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 27 | 0 | 0 | 0
F41ILU | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 32 | 28 | 0 | 0 | 0
F41ILU/T2 | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 32 | 27 | 0 | 0 | 0
F41ILU/T2-R | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 32 | 24 | 0 | 0 | 0
F41ILU/T3 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 32 | 27 | 0 | 0 | 0
F41ILU/T3-R | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 32 | 24 | 0 | 0 | 0
F41ILU/T4 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 32 | 26.75 | 0 | 0 | 0
F41ILU/T4-R | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 32 | 23.75 | 0 | 0 | 0
F41ILU-H | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Prem. Elec. |  | 1 |  | 32 | 35 | 0 | 0 | 0
F41ILU-R | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 32 | 25 | 0 | 0 | 0
F41INLU | Fluorescent, (1), T-8 @ 25W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 25 | 23 | 0 | 0 | 0
F41INLU/T3-R | Fluorescent, (1) 48", T-8 @ 25W lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 25 | 19 | 0 | 0 | 0
F41INLU/T4-R | Fluorescent, (1) 48", T-8 @ 25W lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 25 | 18.75 | 0 | 0 | 0
F41INLU-R | Fluorescent, (1), T-8 @ 25W lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 25 | 21 | 0 | 0 | 0
F41INLU-V | Fluorescent, (1), T-8 @ 25W lamp, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 1 |  | 25 | 32 | 0 | 0 | 0
F41IRLL | Fluorescent, (1) 48", T-8 @ 28W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 28 | 27 | 0 | 0 | 0
F41IRLL-V | Fluorescent, (1) 48" T-8 @ 28W lamp, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 1 |  | 28 | 35 | 0 | 0 | 0
F41IRLU | Fluorescent, (1), T-8 @ 28W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 28 | 25 | 0 | 0 | 0
F41IRLU/T3-R | Fluorescent, (1) 48", T-8 @ 28W lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 28 | 21 | 0 | 0 | 0
F41IRLU/T4-R | Fluorescent, (1) 48", T-8 @ 28W lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 28 | 20.75 | 0 | 0 | 0
F41IRLU-R | Fluorescent, (1), T-8 @ 28W lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 28 | 22 | 0 | 0 | 0
F41IRLU-V | Fluorescent, (1), T-8 @ 28W lamp, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 1 |  | 28 | 33 | 0 | 0 | 0
F41LE | Fluorescent, (1) 48", T-8 lamp | Mag-ES |  | 1 |  | 32 | 35 | 0 | 0 | 0
F41LHL | Fluorescent, (1) 48", T-8 HO lamps, (1) Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 44 | 59 | 0 | 0 | 0
F41LL | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 32 | 0 | 0 | 0
F41LL/T2 | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 30 | 0 | 0 | 0
F41LL/T2-H | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp RS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 32 | 35 | 0 | 0 | 0
F41LL/T2-R | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp RS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 27 | 0 | 0 | 0
F41LL/T3 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 31 | 0 | 0 | 0
F41LL/T3-H | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp RS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 32 | 32.6667 | 0 | 0 | 0
F41LL/T3-R | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp RS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 25.3333 | 0 | 0 | 0
F41LL/T4 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 29.5 | 0 | 0 | 0
F41LL/T4-R | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp RS Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 26.25 | 0 | 0 | 0
F41LL-H | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 32 | 39 | 0 | 0 | 0
F41LL-R | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 27 | 0 | 0 | 0
Intentionally Blank
F42GELL | Fluorescent (2) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 2 |  | 30 | 56 | 0 | 0 | 0
F42GELL-R | Fluorescent (2) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 2 |  | 30 | 43 | 0 | 0 | 0
F42GLL | Fluorescent (2) 48" T-8 lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 2 |  | 32 | 59 | 0 | 0 | 0
F42GLL-R | Fluorescent (2) 48" T-8 lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 2 |  | 32 | 47 | 0 | 0 | 0
F42GLL-V | Fluorescent, (2) 48" T-8 lamps, Prog. Start or PRS Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 32 | 74 | 0 | 0 | 0
F42GNLL | Fluorescent (2) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 2 |  | 25 | 44 | 0 | 0 | 0
F42GNLL-R | Fluorescent (2) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 2 |  | 25 | 38 | 0 | 0 | 0
F42GRLL | Fluorescent (2) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 2 |  | 28 | 49 | 0 | 0 | 0
F42GRLL-R | Fluorescent (2) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 2 |  | 28 | 40 | 0 | 0 | 0
F42IELL | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 30 | 55 | 0 | 0 | 0
Intentionally Blank
F42IELL/T4 | Fluorescent (4) 48" T-8 @ 30W lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 30 | 53 | 0 | 0 | 0
F42IELL/T4-R | Fluorescent (4) 48" T-8 @ 30W lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 30 | 46 | 0 | 0 | 0
Intentionally Blank
F42IELL-H | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 2 |  | 30 | 62 | 0 | 0 | 0
F42IELL-R | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 30 | 49 | 0 | 0 | 0
F42IELU | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 30 | 52 | 0 | 0 | 0
F42IELU/T4 | Fluorescent (2) 48" T-8 @ 30W lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 30 | 50.5 | 0 | 0 | 0
F42IELU/T4-R | Fluorescent (2) 48" T-8 @ 30W lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 30 | 44.5 | 0 | 0 | 0
F42IELU-R | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 30 | 45 | 0 | 0 | 0
F42IELU-V | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start, VHLO (BF > 1.1) | Prem. Elec. |  | 2 |  | 30 | 70 | 0 | 0 | 0
F42ILL | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 58 | 0 | 0 | 0
F42ILL/2 | Fluorescent, (2) 48", T-8 lamps, (2) 1-lamp Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 62 | 0 | 0 | 0
F42ILL/2-R | Fluorescent, (2) 48" T-8 lamps, (2) 1-lamp Instant Start Ballasts, RLO (BF< 0.85) | Electronic |  | 2 |  | 32 | 54 | 0 | 0 | 0
F42ILL/T4 | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 56 | 0 | 0 | 0
F42ILL/T4-R | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 32 | 49 | 0 | 0 | 0
F42ILL-H | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 2 |  | 32 | 66 | 0 | 0 | 0
F42ILL-R | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 32 | 51 | 0 | 0 | 0
F42ILL-V | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 32 | 77 | 0 | 0 | 0
F42ILU | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 32 | 54 | 0 | 0 | 0
F42ILU/T4 | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 32 | 53.5 | 0 | 0 | 0
F42ILU/T4-R | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 32 | 47.5 | 0 | 0 | 0
F42ILU-R | Fluorescent, (2) 48", T-8 lamps, Instant Start, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 32 | 48 | 0 | 0 | 0
F42ILU-V | Fluorescent, (2) 48", T-8 lamps, Instant Start, VHLO (BF> 1.1) | Prem. Elec. |  | 2 |  | 32 | 73 | 0 | 0 | 0
F42INLL | Fluorescent, (2) 48", T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 46 | 0 | 0 | 0
F42INLL-V | Fluorescent, (2) 48" T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 25 | 65 | 0 | 0 | 0
F42INLU | Fluorescent, (2), T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 25 | 43 | 0 | 0 | 0
F42INLU/T4-R | Fluorescent, (2) 48", T-8 @ 25W lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 25 | 37.5 | 0 | 0 | 0
F42INLU-R | Fluorescent (2) 48" T8 @ 25W lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 25 | 38 | 0 | 0 | 0
F42INLU-V | Fluorescent, (2) 48", T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 2 |  | 25 | 60 | 0 | 0 | 0
F42IRLL | Fluorescent, (2) 48", T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 28 | 52 | 0 | 0 | 0
F42IRLL-V | Fluorescent, (2) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 28 | 68 | 0 | 0 | 0
F42IRLU | Fluorescent, (2), T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 28 | 48 | 0 | 0 | 0
F42IRLU/T4-R | Fluorescent, (2) 48", T-8 @ 28W lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 28 | 41.5 | 0 | 0 | 0
F42IRLU-R | Fluorescent, (2) 48", T-8 @ 28W lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 28 | 43 | 0 | 0 | 0
F42IRLU-V | Fluorescent, (2) 48", T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 2 |  | 28 | 65 | 0 | 0 | 0
F42LE | Fluorescent, (2) 48", T-8 lamp | Mag-ES |  | 2 |  | 32 | 71 | 0 | 0 | 0
F42LHL | Fluorescent, (2) 48", T-8 HO lamps, (1) Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 44 | 98 | 0 | 0 | 0
F42LL | Fluorescent, (2) 48", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 60 | 0 | 0 | 0
F42LL/2 | Fluorescent, (2) 48", T-8 lamps, (2) 1-lamp Rapid Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 64 | 0 | 0 | 0
F42LL/T4 | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 59 | 0 | 0 | 0
F42LL/T4-R | Fluorescent, (2) 48", T-8 lamp, Tandem 4-lamp RS Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 32 | 52.5 | 0 | 0 | 0
F42LL-H | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 2 |  | 32 | 70 | 0 | 0 | 0
F42LL-R | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 32 | 54 | 0 | 0 | 0
F42LL-V | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 32 | 85 | 0 | 0 | 0
Intentionally Blank
F43GELL | Fluorescent (3) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 3 |  | 30 | 83 | 0 | 0 | 0
F43GELL-R | Fluorescent (3) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 3 |  | 30 | 67 | 0 | 0 | 0
F43GLL | Fluorescent (3) 48" T-8 lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 3 |  | 32 | 88 | 0 | 0 | 0
F43GLL-R | Fluorescent (3) 48" T-8 lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 3 |  | 32 | 72 | 0 | 0 | 0
F43GLL-V | Fluorescent, (3) 48" T-8 lamps, Prog. Start or PRS Ballast, VHLO (BF > 1.1) | Electronic |  | 3 |  | 32 | 108 | 0 | 0 | 0
F43GNLL | Fluorescent (3) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 3 |  | 25 | 66 | 0 | 0 | 0
F43GNLL-R | Fluorescent, (3) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 3 |  | 25 | 56 | 0 | 0 | 0
F43GRLL | Fluorescent (3) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 3 |  | 28 | 75 | 0 | 0 | 0
F43GRLL-R | Fluorescent, (3) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 3 |  | 28 | 62 | 0 | 0 | 0
F43IELL | Fluorescent (3) 48" T-8 @ 30 W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 30 | 81 | 0 | 0 | 0
F43IELL/2 | Fluorescent (3) 48" T-8 @ 30 W lamps, (1) 1-lamp and (1) 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 30 | 84 | 0 | 0 | 0
F43IELL/2-H | Fluorescent (3) 48" T-8 @ 30 W lamps, (1) 2-lamp, (1) 3-lamp IS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic |  | 3 |  | 30 | 96 | 0 | 0 | 0
F43IELL/2-R | Fluorescent (3) 48" T-8 @ 30 W lamps, (1) 1-lamp and (1) 2-lamp IS Ballast, RLO (BF < 0.85) | Electronic |  | 3 |  | 30 | 75 | 0 | 0 | 0
F43IELL-H | Fluorescent (3) 48" T-8 @ 30 W lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 3 |  | 30 | 86 | 0 | 0 | 0
F43IELL-R | Fluorescent (3) 48" T-8 @ 30 W lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 3 |  | 30 | 71 | 0 | 0 | 0
F43IELU | Fluorescent (3) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 30 | 77 | 0 | 0 | 0
F43IELU-R | Fluorescent (3) 48" T-8 @ 30W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 3 |  | 30 | 68 | 0 | 0 | 0
F43IELU-V | Fluorescent (3) 48" T-8 @ 30W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 3 |  | 30 | 104 | 0 | 0 | 0
F43ILL | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 32 | 85 | 0 | 0 | 0
F43ILL/2 | Fluorescent, (3) 48" T-8 lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 32 | 89 | 0 | 0 | 0
F43ILL/2-H | Fluorescent (3) 48" T-8 lamps, (1) 2-lamp and (1) 3-lamp IS Ballast,1 lead capped, HLO (0.95 < BF < 1.1) | Electronic |  | 3 |  | 32 | 102 | 0 | 0 | 0
F43ILL/2-R | Fluorescent, (3) 48" T-8 lamps, (1) 1-lamp and (1) 2-lamp IS Ballast, RLO (BF < 0.85) | Electronic |  | 3 |  | 32 | 78 | 0 | 0 | 0
F43ILL-H | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 3 |  | 32 | 93 | 0 | 0 | 0
F43ILL-R | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 3 |  | 32 | 76 | 0 | 0 | 0
F43ILL-V | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 3 |  | 32 | 112 | 0 | 0 | 0
F43ILU | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 32 | 81 | 0 | 0 | 0
F43ILU-R | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 3 |  | 32 | 72 | 0 | 0 | 0
F43ILU-V | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 3 |  | 32 | 108 | 0 | 0 | 0
F43INLL | Fluorescent, (3) 48" T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 25 | 66 | 0 | 0 | 0
F43INLL-V | Fluorescent, (3) 48" T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 3 |  | 25 | 95 | 0 | 0 | 0
F43INLU | Fluorescent, (3) 48" T-8 lamps @ 25W, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 25 | 64 | 0 | 0 | 0
F43INLU-R | Fluorescent, (3) 48" T-8 @ 25W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 3 |  | 25 | 57 | 0 | 0 | 0
F43INLU-V | Fluorescent, (3) 48" T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 3 |  | 25 | 93 | 0 | 0 | 0
F43IRLL | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 28 | 76 | 0 | 0 | 0
F43IRLL-H | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, HLO (.95 < BF < 1.1) | Electronic |  | 3 |  | 28 | 82 | 0 | 0 | 0
F43IRLL-V | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 3 |  | 28 | 97 | 0 | 0 | 0
F43IRLU | Fluorescent, (3) 48" T-8 lamps @ 28W, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 28 | 72 | 0 | 0 | 0
F43IRLU-R | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 3 |  | 28 | 63 | 0 | 0 | 0
F43IRLU-V | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 3 |  | 28 | 96 | 0 | 0 | 0
F43LE | Fluorescent, (3) 48", T-8 lamp | Mag-ES |  | 3 |  | 32 | 110 | 0 | 0 | 0
F43LHL | Fluorescent, (3) 48", T-8 HO lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 44 | 141 | 0 | 0 | 0
F43LL | Fluorescent, (3) 48", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 32 | 93 | 0 | 0 | 0
F43LL/2 | Fluorescent, (3) 48", T-8 lamps, (1) 1-lamp and (1) 2-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 32 | 92 | 0 | 0 | 0
F43LL-H | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, HLO (.95 < BF < 1.1) | Electronic |  | 3 |  | 32 | 98 | 0 | 0 | 0
F43LL-R | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, RLO (BF < 0.85) | Electronic |  | 3 |  | 32 | 76 | 0 | 0 | 0
Intentionally Blank
F44GELL | Fluorescent (4) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 4 |  | 30 | 109 | 0 | 0 | 0
F44GELL-R | Fluorescent (4) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 4 |  | 30 | 86 | 0 | 0 | 0
F44GLL | Fluorescent (4) 48" T-8 lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 4 |  | 32 | 115 | 0 | 0 | 0
F44GLL-R | Fluorescent (4) 48" T-8 lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 4 |  | 32 | 92 | 0 | 0 | 0
F44GLL-V | Fluorescent, (4) 48" T-8 lamps, Prog. Start or PRS Ballast, VHLO (BF > 1.1) | Electronic |  | 4 |  | 32 | 144 | 0 | 0 | 0
F44GNLL | Fluorescent (4) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 4 |  | 25 | 85 | 0 | 0 | 0
F44GNLL-R | Fluorescent (4) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 4 |  | 25 | 73 | 0 | 0 | 0
F44GRLL | Fluorescent (4) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 4 |  | 28 | 99 | 0 | 0 | 0
F44GRLL-R | Fluorescent (4) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 4 |  | 28 | 80 | 0 | 0 | 0
F44IELL | Fluorescent (4) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 30 | 106 | 0 | 0 | 0
F44IELL/2 | Fluorescent (4) 48" T-8 @ 30W lamps, (2) 2-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 30 | 110 | 0 | 0 | 0
F44IELL/2-H | Fluorescent (4) 48" T-8 @ 30W lamps, (2) 3-lamp IS Ballasts, 1 lead capped, HLO (.95 < BF < 1.1) | Electronic |  | 4 |  | 30 | 124 | 0 | 0 | 0
F44IELL/2-R | Fluorescent (4) 48" T-8 @ 30W lamps, (2) 2-lamp IS Ballasts, RLO (BF< 0.85) | Electronic |  | 4 |  | 30 | 98 | 0 | 0 | 0
F44IELL-R | Fluorescent (4) 48" T-8 @ 30W lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 4 |  | 30 | 92 | 0 | 0 | 0
F44IELU | Fluorescent (4) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 30 | 101 | 0 | 0 | 0
F44IELU-R | Fluorescent (4) 48" T-8 @ 30W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 4 |  | 30 | 89 | 0 | 0 | 0
F44ILL | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 32 | 112 | 0 | 0 | 0
F44ILL/2 | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 32 | 116 | 0 | 0 | 0
F44ILL/2-H | Fluorescent, (4) 48", T-8 lamps, (2) 3-lamp IS Ballasts, 1 lead capped, HLO (.95 < BF < 1.1) | Electronic |  | 4 |  | 32 | 132 | 0 | 0 | 0
F44ILL/2-R | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp IS Ballasts, RLO (BF < 0.85) | Electronic |  | 4 |  | 32 | 102 | 0 | 0 | 0
F44ILL/2-V | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp IS Ballasts, VHLO (BF > 1.1) | Electronic |  | 4 |  | 32 | 154 | 0 | 0 | 0
F44ILL-R | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 4 |  | 32 | 98 | 0 | 0 | 0
F44ILL-V | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 4 |  | 32 | 151 | 0 | 0 | 0
F44ILU | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 32 | 107 | 0 | 0 | 0
F44ILU-R | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 4 |  | 32 | 95 | 0 | 0 | 0
F44ILU-V | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 4 |  | 32 | 146 | 0 | 0 | 0
F44INLL | Fluorescent, (4) 48", T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 25 | 86 | 0 | 0 | 0
F44INLU | Fluorescent, (4) 48", T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 25 | 85 | 0 | 0 | 0
F44INLU-R | Fluorescent, (4) 48" T-8 @ 25W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 4 |  | 25 | 75 | 0 | 0 | 0
F44INLU-V | Fluorescent, (4) 48" T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 4 |  | 25 | 122 | 0 | 0 | 0
F44IRLL | Fluorescent, (4) 48", T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 28 | 99 | 0 | 0 | 0
F44IRLL-R | Fluorescent, (4) 48", T-8 @ 28W lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 4 |  | 28 | 85 | 0 | 0 | 0
F44IRLU | Fluorescent, (4) 48", T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 28 | 94 | 0 | 0 | 0
F44IRLU-R | Fluorescent, (4) 48" T-8 @ 28W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 4 |  | 28 | 83 | 0 | 0 | 0
F44IRLU-V | Fluorescent, (4) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 4 |  | 28 | 131 | 0 | 0 | 0
F44LE | Fluorescent, (4) 48", T-8 lamps | Mag-ES |  | 4 |  | 32 | 142 | 0 | 0 | 0
F44LHL | Fluorescent, (4) 48", T-8 HO lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 44 | 168 | 0 | 0 | 0
F44LL | Fluorescent, (4) 48", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 32 | 118 | 0 | 0 | 0
F44LL/2 | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 32 | 120 | 0 | 0 | 0
F44LL-R | Fluorescent, (4) 48", T-8 lamps, Rapid Start Ballast, RLO (BF < 0.85) | Electronic |  | 4 |  | 32 | 105 | 0 | 0 | 0
Intentionally Blank
F45ILL/2 | Fluorescent, (5) 48", T-8 lamps, (1) 3-lamp and (1) 2-lamp IS ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 5 |  | 32 | 143 | 0 | 0 | 0
F45GLL/2-V | Fluorescent, (5) 48", T-8 lamps, (1) 3-lamp and (1) 2-lamp Prog. Start Ballast, VHLO (BF > 1.1) | Electronic |  | 5 |  | 32 | 182 | 0 | 0 | 0
Intentionally Blank
F46GLL/2 | Fluorescent (6) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 6 |  | 32 | 175 | 0 | 0 | 0
F46GLL/2-R | Fluorescent (6) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, RLO (BF < 0.85) | PRS Elec. |  | 6 |  | 32 | 141.5 | 0 | 0 | 0
F46GLL/2-V | Fluorescent (6) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, VHLO (BF > 1.1) | PRS Elec. |  | 6 |  | 32 | 217 | 0 | 0 | 0
F46IELU/2 | Fluorescent (6) 48" T-8 @ 30W lamps, (2) IS Ballasts, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 6 |  | 30 | 153.5 | 0 | 0 | 0
F46IELU/2-R | Fluorescent (6) 48" T-8 @ 30W lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. |  | 6 |  | 30 | 135 | 0 | 0 | 0
F46ILL/2 | Fluorescent, (6) 48", T-8 lamps, (2) IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 6 |  | 32 | 170 | 0 | 0 | 0
F46ILL/2-R | Fluorescent, (6) 48", T-8 lamps, (2) IS Ballasts, RLO (BF < 0.85) | Electronic |  | 6 |  | 32 | 150.5 | 0 | 0 | 0
F46ILL/2-V | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, VHLO (BF > 1.1) | Electronic |  | 6 |  | 32 | 226 | 0 | 0 | 0
F46ILU/2 | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 6 |  | 32 | 161.5 | 0 | 0 | 0
F46ILU/2-R | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. |  | 6 |  | 32 | 143.5 | 0 | 0 | 0
F46ILU/2-V | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, VHLO (BF > 1.1) | Prem. Elec. |  | 6 |  | 32 | 217.5 | 0 | 0 | 0
F46INLU/2-R | Fluorescent (6) 48" T-8 @ 25W lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. |  | 6 |  | 25 | 113.5 | 0 | 0 | 0
F46INLU/2-V | Fluorescent (6) 48" T-8 @ 25W lamps, (2) IS Ballasts, VHLO (BF > 1.1) | Prem. Elec. |  | 6 |  | 25 | 184 | 0 | 0 | 0
F46IRLU/2-R | Fluorescent (6) 48" T-8 @ 28W lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. |  | 6 |  | 28 | 126 | 0 | 0 | 0
F46IRLU/2-V | Fluorescent (6) 48" T-8 @ 28W lamps, (2) IS Ballasts, VHLO (BF > 1.1) | Prem. Elec. |  | 6 |  | 28 | 194 | 0 | 0 | 0
F46LL/2 | Fluorescent, (6) 48", T-8 lamps, (2) Rapid Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 6 |  | 32 | 182 | 0 | 0 | 0
Intentionally Blank
F48GLL/2 | Fluorescent (8) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 8 |  | 32 | 230 | 0 | 0 | 0
F48GLL/2-R | Fluorescent (8) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, RLO (BF < 0.85) | PRS Elec. |  | 8 |  | 32 | 184 | 0 | 0 | 0
F48GLL/2-V | Fluorescent (8) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, VHLO (BF > 1.1) | PRS Elec. |  | 8 |  | 32 | 288 | 0 | 0 | 0
F48ILL/2 | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 8 |  | 32 | 224 | 0 | 0 | 0
F48ILL/2-R | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, RLO (BF < 0.85) | Electronic |  | 8 |  | 32 | 196 | 0 | 0 | 0
F48ILU/2 | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 8 |  | 32 | 214 | 0 | 0 | 0
F48ILU/2-R | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, RLO (BF < 0.85) | Prem. Elec. |  | 8 |  | 32 | 190 | 0 | 0 | 0
Intentionally Blank
F51ILL | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 40 | 36 | 0 | 0 | 0
F51ILL/T2 | Fluorescent, (1) 60", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 40 | 36 | 0 | 0 | 0
F51ILL/T3 | Fluorescent, (1) 60", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 40 | 35.3333 | 0 | 0 | 0
F51ILL/T4 | Fluorescent, (1) 60", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 40 | 33.5 | 0 | 0 | 0
F51ILL-R | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 1 |  | 40 | 43 | 0 | 0 | 0
Intentionally Blank
F52ILL | Fluorescent, (2) 60", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 40 | 72 | 0 | 0 | 0
F52ILL/T4 | Fluorescent, (2) 60", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 40 | 67 | 0 | 0 | 0
F52ILL-H | Fluorescent, (2) 60", T-8 lamps, Instant Start Ballast, HILO (.95 < BF < 1.1) | Electronic |  | 2 |  | 40 | 80 | 0 | 0 | 0
F52ILL-R | Fluorescent, (2) 60", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 2 |  | 40 | 73 | 0 | 0 | 0
Intentionally Blank
F53ILL | Fluorescent, (3) 60", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 40 | 106 | 0 | 0 | 0
F53ILL-H | Fluorescent, (3) 60", T-8 lamps, Instant Start Ballast, HILO (.95 < BF < 1.1) | Electronic |  | 3 |  | 40 | 108 | 0 | 0 | 0
Intentionally Blank
F54ILL | Fluorescent, (4) 60", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 40 | 134 | 0 | 0 | 0
F54ILL-H | Fluorescent, (4) 60", T-8 lamps, Instant Start Ballast, HILO (.95 < BF < 1.1) | Electronic |  | 4 |  | 40 | 126 | 0 | 0 | 0
Intentionally Blank
F81IELU | Fluorescent, (1) 96" T-8 @ 57W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 57 | 51 | 0 | 0 | 0
F81ILL | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 59 | 65 | 0 | 0 | 0
F81ILL/T2 | Fluorescent, (1) 96", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 59 | 55 | 0 | 0 | 0
F81ILL/T2-R | Fluorescent, (1) 96", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF < 0.85) | Electronic |  | 1 |  | 59 | 49 | 0 | 0 | 0
F81ILL-H | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, HILO (.95 < BF < 1.1) | Electronic |  | 1 |  | 59 | 68 | 0 | 0 | 0
F81ILL-R | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 1 |  | 59 | 57 | 0 | 0 | 0
F81ILL-V | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 1 |  | 59 | 71 | 0 | 0 | 0
F81ILU | Fluorescent, (1) 96" T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 57 | 61 | 0 | 0 | 0
F81LHL/T2 | Fluorescent, (1) 96", T-8 HO lamp, Tandem 2-lamp Ballast | Electronic |  | 1 |  | 86 | 80 | 0 | 0 | 0
Intentionally Blank
F82IELU | Fluorescent, (2) 96" T-8 @ 57W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 57 | 100 | 0 | 0 | 0
F82ILL | Fluorescent, (2) 96", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 59 | 110 | 0 | 0 | 0
F82ILL-R | Fluorescent, (2) 96", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 2 |  | 59 | 98 | 0 | 0 | 0
F82ILL-V | Fluorescent, (2) 96", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 59 | 149 | 0 | 0 | 0
F82ILU | Fluorescent, (2) 96" T-8 ES lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 59 | 107 | 0 | 0 | 0
F82LHL | Fluorescent, (2) 96", T-8 HO lamps | Electronic |  | 2 |  | 86 | 160 | 0 | 0 | 0
Intentionally Blank
F83ILL | Fluorescent, (3) 96", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 59 | 167 | 0 | 0 | 0
Intentionally Blank
F84ILL | Fluorescent, (4) 96", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 59 | 219 | 0 | 0 | 0
F84ILL/2-V | Fluorescent, (4) 96", T-8 lamps, (2) Instant Start Ballasts, VHLO (BF > 1.1) | Electronic |  | 4 |  | 59 | 298 | 0 | 0 | 0
F84LHL | Fluorescent, (4) 96", T-8 HO lamps | Electronic |  | 4 |  | 86 | 320 | 0 | 0 | 0
Intentionally Blank
F86ILL | Fluorescent, (6) 96", T-8 lamps, (2) 3-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 6 |  | 59 | 329.5 | 0 | 0 | 0
(Replacement Fixture)
F21ILL-R | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 17 | 17 | 40 | 75
F21ILU | Fluorescent, (1) 24", T-8 lamp | Prem. Elec. |  | 1 |  | 17 | 17 | 40 | 75
F21ILU-R | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 17 | 15 | 40 | 75
F21ILU-V | Fluorescent, (1) 24", T-8 lamps, Instant Start Ballast, VHLO ( BF > 1.1) | Prem. Elec. |  | 1 |  | 17 | 22 | 40 | 75
F21LL | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 17 | 16 | 40 | 75
F21LL-R | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 17 | 15 | 40 | 75
F21SL | Fluorescent, (1) 24", T-8 lamp, Standard Ballast | Mag-STD |  | 1 |  | 17 | 24 | 40 | 75
Intentionally Blank
F22ILL | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 17 | 33 | 40 | 75
F22ILL-R | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 17 | 30 | 40 | 75
F22ILU | Fluorescent, (2) 24", T-8 lamps | Prem. Elec. |  | 2 |  | 17 | 30 | 40 | 75
F22ILU-R | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 17 | 27 | 40 | 75
F22ILU-V | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, VHLO ( BF > 1.1) | Prem. Elec. |  | 2 |  | 17 | 41 | 40 | 75
F22LL | Fluorescent, (2) 24", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 17 | 31 | 40 | 75
F22LL-R | Fluorescent, (2) 24", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 17 | 28 | 40 | 75
Intentionally Blank
F23ILL | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 17 | 47 | 40 | 100
F23ILL-H | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 3 |  | 17 | 51 | 40 | 100
F23ILL-R | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 3 |  | 17 | 41 | 40 | 100
F23ILU | Fluorescent, (3) 24", T-8 lamps | Prem. Elec. |  | 3 |  | 17 | 45 | 40 | 100
F23ILU-R | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 3 |  | 17 | 40 | 40 | 100
F23ILU-V | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, VHLO ( BF > 1.1) | Prem. Elec. |  | 3 |  | 17 | 59 | 40 | 100
F23LL | Fluorescent, (3) 24", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 17 | 52 | 40 | 100
F23LL-R | Fluorescent, (3) 24", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 3 |  | 17 | 41 | 40 | 100
Intentionally Blank
F24ILL | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 17 | 59 | 40 | 100
F24ILL-R | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 4 |  | 17 | 53 | 40 | 100
F24ILU | Fluorescent, (4) 24", T-8 lamps | Prem. Elec. |  | 4 |  | 17 | 57 | 40 | 100
F24ILU-R | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 4 |  | 17 | 52 | 40 | 100
F24LL | Fluorescent, (4) 24", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 17 | 68 | 40 | 100
F24LL-R | Fluorescent, (4) 24", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 4 |  | 17 | 57 | 40 | 100
Intentionally Blank
F31ILL | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 26 | 40 | 75
F31ILL-H | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 25 | 28 | 40 | 75
F31ILL-R | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 25 | 22 | 40 | 75
F31ILU | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 25 | 23 | 40 | 75
F31ILU-R | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 25 | 20 | 40 | 75
F31LL | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 24 | 40 | 75
F31LL-H | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 25 | 26 | 40 | 75
F31LL-R | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 25 | 23 | 40 | 75
Intentionally Blank
F32ILL | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 46 | 40 | 75
F32ILL/2-R | Fluorescent, (2) 36", T-8 lamps, (2) Instant Start Ballasts, RLO (BF< 0.85) | Electronic |  | 2 |  | 25 | 44 | 40 | 75
F32ILL-H | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 2 |  | 25 | 52 | 40 | 75
F32ILL-R | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 25 | 42 | 40 | 75
F32ILU | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 25 | 44 | 40 | 75
F32ILU-R | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 25 | 39 | 40 | 75
F32LL | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 46 | 40 | 75
F32LL-H | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 2 |  | 25 | 50 | 40 | 75
F32LL-R | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 25 | 42 | 40 | 75
F32LL-V | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 25 | 70 | 40 | 75
Intentionally Blank
F33ILL | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 25 | 68 | 40 | 100
F33ILL-R | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 3 |  | 25 | 61 | 40 | 100
F33ILU | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 25 | 65 | 40 | 100
F33ILU-R | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 3 |  | 25 | 58 | 40 | 100
F33LL | Fluorescent, (3) 36", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 25 | 72 | 40 | 100
F33LL-R | Fluorescent, (3) 36", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 3 |  | 25 | 62 | 40 | 100
Intentionally Blank
F34ILL | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 25 | 88 | 40 | 100
F34ILL/2-R | Fluorescent, (4) 36", T-8 lamps, (2) Instant Start Ballasts, RLO (BF< 0.85) | Electronic |  | 4 |  | 25 | 84 | 40 | 100
F34ILL-R | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 4 |  | 25 | 78 | 40 | 100
F34ILU | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 25 | 86 | 40 | 100
F34ILU-R | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 4 |  | 25 | 77 | 40 | 100
F34LL | Fluorescent, (4) 36", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 25 | 89 | 40 | 100
F34LL-R | Fluorescent, (4) 36", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 4 |  | 25 | 84 | 40 | 100
F36ILL/2 | Fluorescent, (6) 36", T-8 lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 6 |  | 25 | 135 | 0 | 0
F36ILL/2-R | Fluorescent, (6) 36", T-8 lamps, (2) Instant Start Ballasts, RLO (BF< 0.85) | Electronic |  | 6 |  | 25 | 121 | 0 | 0
Intentionally Blank
F41GLL | Fluorescent (1) 48" T-8 lamp, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 1 |  | 32 | 30 | 35 | 75
F41GLL-R | Fluorescent (1) 48" T-8 lamp, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 1 |  | 32 | 25 | 35 | 75
F41GNLL | Fluorescent (1) 48" T-8 @ 25W lamp, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 1 |  | 25 | 24 | 35 | 75
F41GNLL-R | Fluorescent (1) 48" T-8 @ 25W lamp, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 1 |  | 25 | 21 | 35 | 75
F41GRLL | Fluorescent (1) 48" T-8 @ 28W lamp | PRS Elec. |  | 1 |  | 28 | 26 | 35 | 75
F41GRLL-R | Fluorescent (1) 48" T-8 @ 28W lamp, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 1 |  | 28 | 22 | 35 | 75
F41ILL | Fluorescent, (1) 48", T-8 lamp | Electronic |  | 1 |  | 32 | 31 | 35 | 75
F41ILL-H | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 32 | 36 | 35 | 75
F41ILL-R | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 27 | 35 | 75
F41ILU | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 32 | 28 | 35 | 75
F41ILU-H | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Prem. Elec. |  | 1 |  | 32 | 35 | 35 | 75
F41ILU-R | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 32 | 25 | 35 | 75
F41INLU | Fluorescent, (1), T-8 @ 25W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 25 | 23 | 35 | 75
F41INLU-R | Fluorescent, (1), T-8 @ 25W lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 25 | 21 | 35 | 75
F41INLU-V | Fluorescent, (1), T-8 @ 25W lamp, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 1 |  | 25 | 32 | 35 | 75
F41IRLL | Fluorescent, (1) 48", T-8 @ 28W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 28 | 27 | 35 | 75
F41IRLL-V | Fluorescent, (1) 48" T-8 @ 28W lamp, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 1 |  | 28 | 35 | 35 | 75
F41IRLU | Fluorescent, (1), T-8 @ 28W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 28 | 25 | 35 | 75
F41IRLU-R | Fluorescent, (1), T-8 @ 28W lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 1 |  | 28 | 22 | 35 | 75
F41IRLU-V | Fluorescent, (1), T-8 @ 28W lamp, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 1 |  | 28 | 33 | 35 | 75
F41LL | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 32 | 35 | 75
F41LL-H | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 1 |  | 32 | 39 | 35 | 75
F41LL-R | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 1 |  | 32 | 27 | 35 | 75
Intentionally Blank
F42GLL | Fluorescent (2) 48" T-8 lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 2 |  | 32 | 59 | 35 | 75 | 60
F42GLL-R | Fluorescent (2) 48" T-8 lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 2 |  | 32 | 47 | 35 | 75 | 60
F42GLL-V | Fluorescent, (2) 48" T-8 lamps, Prog. Start or PRS Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 32 | 74 | 35 | 75 | 60
F42GNLL | Fluorescent (2) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 2 |  | 25 | 44 | 35 | 75 | 60
F42GNLL-R | Fluorescent (2) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 2 |  | 25 | 38 | 35 | 75 | 60
F42GRLL | Fluorescent (2) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 2 |  | 28 | 49 | 35 | 75 | 60
F42GRLL-R | Fluorescent (2) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. |  | 2 |  | 28 | 40 | 35 | 75 | 60
F42ILL | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 58 | 35 | 75 | 60
F42ILL/2 | Fluorescent, (2) 48", T-8 lamps, (2) 1-lamp Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 62 | 35 | 75 | 60
F42ILL/2-R | Fluorescent, (2) 48" T-8 lamps, (2) 1-lamp Instant Start Ballasts, RLO (BF< 0.85) | Electronic |  | 2 |  | 32 | 54 | 35 | 75 | 60
F42ILL-H | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 2 |  | 32 | 66 | 35 | 75 | 60
F42ILL-R | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 32 | 51 | 35 | 75 | 60
F42ILL-V | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 32 | 77 | 35 | 75 | 60
F42ILU | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 32 | 54 | 35 | 75 | 60
F42ILU-R | Fluorescent, (2) 48", T-8 lamps, Instant Start, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 32 | 48 | 35 | 75 | 60
F42ILU-V | Fluorescent, (2) 48", T-8 lamps, Instant Start, VHLO (BF> 1.1) | Prem. Elec. |  | 2 |  | 32 | 73 | 35 | 75 | 60
F42INLL | Fluorescent, (2) 48", T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 46 | 35 | 75 | 60
F42INLL-V | Fluorescent, (2) 48" T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 25 | 65 | 35 | 75 | 60
F42INLU | Fluorescent, (2), T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 25 | 43 | 35 | 75 | 60
F42INLU-R | Fluorescent (2) 48" T8 @ 25W lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 25 | 38 | 35 | 75 | 60
F42INLU-V | Fluorescent, (2) 48", T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 2 |  | 25 | 60 | 35 | 75 | 60
F42IRLL | Fluorescent, (2) 48", T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 28 | 52 | 35 | 75 | 60
F42IRLL-V | Fluorescent, (2) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 28 | 68 | 35 | 75 | 60
F42IRLU | Fluorescent, (2), T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 28 | 48 | 35 | 75 | 60
F42IRLU-R | Fluorescent, (2) 48", T-8 @ 28W lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. |  | 2 |  | 28 | 43 | 35 | 75 | 60
F42IRLU-V | Fluorescent, (2) 48", T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 2 |  | 28 | 65 | 35 | 75 | 60
F42LL | Fluorescent, (2) 48", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 60 | 35 | 75 | 60
F42LL/2 | Fluorescent, (2) 48", T-8 lamps, (2) 1-lamp Rapid Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 64 | 35 | 75 | 60
F42LL-H | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 2 |  | 32 | 70 | 35 | 75 | 60
F42LL-R | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic |  | 2 |  | 32 | 54 | 35 | 75 | 60
F42LL-V | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, VHLO (BF > 1.1) | Electronic |  | 2 |  | 32 | 85 | 35 | 75 | 60
Intentionally Blank
F43GLL | Fluorescent (3) 48" T-8 lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 3 |  | 32 | 88 | 45 | 95 | 60
F43GLL-R | Fluorescent (3) 48" T-8 lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 3 |  | 32 | 72 | 45 | 95 | 60
F43GLL-V | Fluorescent, (3) 48" T-8 lamps, Prog. Start or PRS Ballast, VHLO (BF > 1.1) | Electronic |  | 3 |  | 32 | 108 | 45 | 95 | 60
F43GNLL | Fluorescent (3) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 3 |  | 25 | 66 | 45 | 95 | 60
F43GNLL-R | Fluorescent, (3) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 3 |  | 25 | 56 | 45 | 95 | 60
F43GRLL | Fluorescent (3) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 3 |  | 28 | 75 | 45 | 95 | 60
F43GRLL-R | Fluorescent, (3) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 3 |  | 28 | 62 | 45 | 95 | 60
F43ILL | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 32 | 85 | 45 | 95 | 60
F43ILL/2 | Fluorescent, (3) 48" T-8 lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 32 | 89 | 45 | 95 | 60
F43ILL/2-H | Fluorescent (3) 48" T-8 lamps, (1) 2-lamp and (1) 3-lamp IS Ballast,1 lead capped, HLO (0.95 < BF < 1.1) | Electronic |  | 3 |  | 32 | 102 | 45 | 95 | 60
F43ILL/2-R | Fluorescent, (3) 48" T-8 lamps, (1) 1-lamp and (1) 2-lamp IS Ballast, RLO (BF < 0.85) | Electronic |  | 3 |  | 32 | 78 | 45 | 95 | 60
F43ILL-H | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic |  | 3 |  | 32 | 93 | 45 | 95 | 60
F43ILL-R | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 3 |  | 32 | 76 | 45 | 95 | 60
F43ILL-V | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 3 |  | 32 | 112 | 45 | 95 | 60
F43ILU | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 32 | 81 | 45 | 95 | 60
F43ILU-R | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 3 |  | 32 | 72 | 45 | 95 | 60
F43ILU-V | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 3 |  | 32 | 108 | 45 | 95 | 60
F43INLL | Fluorescent, (3) 48" T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 25 | 66 | 45 | 95 | 60
F43INLL-V | Fluorescent, (3) 48" T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 3 |  | 25 | 95 | 45 | 95 | 60
F43INLU | Fluorescent, (3) 48" T-8 lamps @ 25W, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 25 | 64 | 45 | 95 | 60
F43INLU-R | Fluorescent, (3) 48" T-8 @ 25W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 3 |  | 25 | 57 | 45 | 95 | 60
F43INLU-V | Fluorescent, (3) 48" T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 3 |  | 25 | 93 | 45 | 95 | 60
F43IRLL | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 28 | 76 | 45 | 95 | 60
F43IRLL-H | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, HLO (.95 < BF < 1.1) | Electronic |  | 3 |  | 28 | 82 | 45 | 95 | 60
F43IRLL-V | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 3 |  | 28 | 97 | 45 | 95 | 60
F43IRLU | Fluorescent, (3) 48" T-8 lamps @ 28W, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 3 |  | 28 | 72 | 45 | 95 | 60
F43IRLU-R | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 3 |  | 28 | 63 | 45 | 95 | 60
F43IRLU-V | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 3 |  | 28 | 96 | 45 | 95 | 60
F43LL | Fluorescent, (3) 48", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 32 | 93 | 45 | 95 | 60
F43LL/2 | Fluorescent, (3) 48", T-8 lamps, (1) 1-lamp and (1) 2-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 3 |  | 32 | 92 | 45 | 95 | 60
F43LL-H | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, HLO (.95 < BF < 1.1) | Electronic |  | 3 |  | 32 | 98 | 45 | 95 | 60
F43LL-R | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, RLO (BF < 0.85) | Electronic |  | 3 |  | 32 | 76 | 45 | 95 | 60
Intentionally Blank
F44GLL | Fluorescent (4) 48" T-8 lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 4 |  | 32 | 115 | 45 | 95 | 60
F44GLL-R | Fluorescent (4) 48" T-8 lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 4 |  | 32 | 92 | 45 | 95 | 60
F44GLL-V | Fluorescent, (4) 48" T-8 lamps, Prog. Start or PRS Ballast, VHLO (BF > 1.1) | Electronic |  | 4 |  | 32 | 144 | 45 | 95 | 60
F44GNLL | Fluorescent (4) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 4 |  | 25 | 85 | 45 | 95 | 60
F44GNLL-R | Fluorescent (4) 48" T-8 @ 25W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 4 |  | 25 | 73 | 45 | 95 | 60
F44GRLL | Fluorescent (4) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 4 |  | 28 | 99 | 45 | 95 | 60
F44GRLL-R | Fluorescent (4) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. |  | 4 |  | 28 | 80 | 45 | 95 | 60
F44ILL | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 32 | 112 | 45 | 95 | 60
F44ILL/2 | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 32 | 116 | 45 | 95 | 60
F44ILL/2-H | Fluorescent, (4) 48", T-8 lamps, (2) 3-lamp IS Ballasts, 1 lead capped, HLO (.95 < BF < 1.1) | Electronic |  | 4 |  | 32 | 132 | 45 | 95 | 60
F44ILL/2-R | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp IS Ballasts, RLO (BF < 0.85) | Electronic |  | 4 |  | 32 | 102 | 45 | 95 | 60
F44ILL/2-V | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp IS Ballasts, VHLO (BF > 1.1) | Electronic |  | 4 |  | 32 | 154 | 45 | 95 | 60
F44ILL-R | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 4 |  | 32 | 98 | 45 | 95 | 60
F44ILL-V | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic |  | 4 |  | 32 | 151 | 45 | 95 | 60
F44ILU | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 32 | 107 | 45 | 95 | 60
F44ILU-R | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 4 |  | 32 | 95 | 45 | 95 | 60
F44ILU-V | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 4 |  | 32 | 146 | 45 | 95 | 60
F44INLL | Fluorescent, (4) 48", T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 25 | 86 | 45 | 95 | 60
F44INLU | Fluorescent, (4) 48", T-8 @ 25W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 25 | 85 | 45 | 95 | 60
F44INLU-R | Fluorescent, (4) 48" T-8 @ 25W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 4 |  | 25 | 75 | 45 | 95 | 60
F44INLU-V | Fluorescent, (4) 48" T-8 @ 25W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 4 |  | 25 | 122 | 45 | 95 | 60
F44IRLL | Fluorescent, (4) 48", T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 28 | 99 | 45 | 95 | 60
F44IRLL-R | Fluorescent, (4) 48", T-8 @ 28W lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 4 |  | 28 | 85 | 45 | 95 | 60
F44IRLU | Fluorescent, (4) 48", T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 4 |  | 28 | 94 | 45 | 95 | 60
F44IRLU-R | Fluorescent, (4) 48" T-8 @ 28W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 4 |  | 28 | 83 | 45 | 95 | 60
F44IRLU-V | Fluorescent, (4) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 4 |  | 28 | 131 | 45 | 95 | 60
F44LE | Fluorescent, (4) 48", T-8 lamps | Mag-ES |  | 4 |  | 32 | 142 | 45 | 95 | 60
F44LL | Fluorescent, (4) 48", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 32 | 118 | 45 | 95 | 60
F44LL/2 | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 4 |  | 32 | 120 | 45 | 95 | 60
F44LL-R | Fluorescent, (4) 48", T-8 lamps, Rapid Start Ballast, RLO (BF < 0.85) | Electronic |  | 4 |  | 32 | 105 | 45 | 95 | 60
Intentionally Blank
F45ILL/2 | Fluorescent, (5) 48", T-8 lamps, (1) 3-lamp and (1) 2-lamp IS ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 5 |  | 32 | 143 | 75 | 210 | 0
F45GLL/2-V | Fluorescent, (5) 48", T-8 lamps, (1) 3-lamp and (1) 2-lamp Prog. Start Ballast, VHLO (BF > 1.1) | Electronic |  | 5 |  | 32 | 182 | 75 | 210 | 0
Intentionally Blank
F46GLL/2 | Fluorescent (6) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 6 |  | 32 | 175 | 75 | 210 | 0
F46GLL/2-R | Fluorescent (6) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, RLO (BF < 0.85) | PRS Elec. |  | 6 |  | 32 | 141.5 | 75 | 210 | 0
F46GLL/2-V | Fluorescent (6) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, VHLO (BF > 1.1) | PRS Elec. |  | 6 |  | 32 | 217 | 75 | 210 | 0
F46ILL/2 | Fluorescent, (6) 48", T-8 lamps, (2) IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 6 |  | 32 | 170 | 75 | 210 | 0
F46ILL/2-R | Fluorescent, (6) 48", T-8 lamps, (2) IS Ballasts, RLO (BF < 0.85) | Electronic |  | 6 |  | 32 | 150.5 | 75 | 210 | 0
F46ILL/2-V | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, VHLO (BF > 1.1) | Electronic |  | 6 |  | 32 | 226 | 75 | 210 | 0
F46ILU/2 | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 6 |  | 32 | 161.5 | 75 | 210 | 0
F46ILU/2-R | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. |  | 6 |  | 32 | 143.5 | 75 | 210 | 0
F46ILU/2-V | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, VHLO (BF > 1.1) | Prem. Elec. |  | 6 |  | 32 | 217.5 | 75 | 210 | 0
F46INLU/2-R | Fluorescent (6) 48" T-8 @ 25W lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. |  | 6 |  | 25 | 113.5 | 75 | 210 | 0
F46INLU/2-V | Fluorescent (6) 48" T-8 @ 25W lamps, (2) IS Ballasts, VHLO (BF > 1.1) | Prem. Elec. |  | 6 |  | 25 | 184 | 75 | 210 | 0
F46IRLU/2-R | Fluorescent (6) 48" T-8 @ 28W lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. |  | 6 |  | 28 | 126 | 75 | 210 | 0
F46IRLU/2-V | Fluorescent (6) 48" T-8 @ 28W lamps, (2) IS Ballasts, VHLO (BF > 1.1) | Prem. Elec. |  | 6 |  | 28 | 194 | 75 | 210 | 0
F46LL/2 | Fluorescent, (6) 48", T-8 lamps, (2) Rapid Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 6 |  | 32 | 182 | 75 | 210 | 0
Intentionally Blank
F48GLL/2 | Fluorescent (8) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, NLO (0.85 < BF < 0.95) | PRS Elec. |  | 8 |  | 32 | 230 | 75 | 210 | 0
F48GLL/2-R | Fluorescent (8) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, RLO (BF < 0.85) | PRS Elec. |  | 8 |  | 32 | 184 | 75 | 210 | 0
F48GLL/2-V | Fluorescent (8) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, VHLO (BF > 1.1) | PRS Elec. |  | 8 |  | 32 | 288 | 75 | 210 | 0
F48ILL/2 | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic |  | 8 |  | 32 | 224 | 75 | 210 | 0
F48ILL/2-R | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, RLO (BF < 0.85) | Electronic |  | 8 |  | 32 | 196 | 75 | 210 | 0
F48ILU/2 | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 8 |  | 32 | 214 | 75 | 210 | 0
F48ILU/2-R | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, RLO (BF < 0.85) | Prem. Elec. |  | 8 |  | 32 | 190 | 75 | 210 | 0
HPT8
(Replacement Fixture)
HPT8(1-F032)LBF | Fluorescent, (1) 48", HPT8 32W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 1 |  | 32 | 25 | 35 | 75
HPT8(1-F032)NBF | Fluorescent, (1) 48", HPT8 32W lamp, Instant or Program Start Ballast, (0.85 < BF < 0.95) | Electronic |  | 1 |  | 32 | 28 | 35 | 75
HPT8(1-F032)HBF | Fluorescent, (1) 48", HPT8 32W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 1 |  | 32 | 38 | 35 | 75
RWT8(1-F028)LBF | Fluorescent, (1) 48", HPT8 28W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 1 |  | 28 | 22 | 35 | 75
RWT8(1-F028)NBF | Fluorescent, (1) 48", HPT8 28W lamp | Electronic |  | 1 |  | 28 | 25 | 35 | 75
RWT8(1-F028)HBF | Fluorescent, (1) 48", HPT8 28W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 1 |  | 28 | 33 | 35 | 75
RWT8(1-F025)LBF | Fluorescent, (1) 48", HPT8 25W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 1 |  | 25 | 22 | 35 | 75
RWT8(1-F025)NBF | Fluorescent, (1) 48", HPT8 25W lamp, Instant or Program Start Ballast, (0.85 < BF < 0.95) | Electronic |  | 1 |  | 25 | 25 | 35 | 75
RWT8(1-F025)HBF | Fluorescent, (1) 48", HPT8 25W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 1 |  | 25 | 33 | 35 | 75
Intentionally Blank
HPT8(2-F032)LBF | Fluorescent, (2) 48", HPT8 32W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 2 |  | 32 | 48 | 35 | 75
HPT8(2-F032)NBF | Fluorescent, (2) 48", HPT8 32W lamp, Instant or Program Start Ballast, (0.85 < BF < 0.95) | Electronic |  | 2 |  | 32 | 55 | 35 | 75
HPT8(2-F032)HBF | Fluorescent, (2) 48", HPT8 32W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 2 |  | 32 | 74 | 35 | 75
RWT8(2-F028)LBF | Fluorescent, (2) 48", HPT8 28W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 2 |  | 28 | 42 | 35 | 75
RWT8(2-F028)NBF | Fluorescent, (2) 48", HPT8 28W lamp | Electronic |  | 2 |  | 28 | 48 | 35 | 75
RWT8(2-F028)HBF | Fluorescent, (2) 48", HPT8 28W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 2 |  | 28 | 65 | 35 | 75
RWT8(2-F025)LBF | Fluorescent, (2) 48", HPT8 25W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 2 |  | 25 | 42 | 35 | 75
RWT8(2-F025)NBF | Fluorescent, (2) 48", HPT8 25W lamp, Instant or Program Start Ballast, (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 48 | 35 | 75
RWT8(2-F025)HBF | Fluorescent, (2) 48", HPT8 25W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 2 |  | 25 | 65 | 35 | 75
Intentionally Blank
HPT8(3-F032)LBF | Fluorescent, (3) 48", HPT8 32W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 3 |  | 32 | 73 | 45 | 95
HPT8(3-F032)NBF | Fluorescent, (3) 48", HPT8 32W lamp, Instant or Program Start Ballast, (0.85 < BF < 0.95) | Electronic |  | 3 |  | 32 | 83 | 45 | 95
HPT8(3-F032)HBF | Fluorescent, (3) 48", HPT8 32W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 3 |  | 32 | 111 | 45 | 95
RWT8(3-F028)LBF | Fluorescent, (3) 48", HPT8 28W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 3 |  | 28 | 63 | 45 | 95
RWT8(3-F028)NBF | Fluorescent, (3) 48", HPT8 28W lamp | Electronic |  | 3 |  | 28 | 72 | 45 | 95
RWT8(3-F028)HBF | Fluorescent, (3) 48", HPT8 28W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 3 |  | 28 | 98 | 45 | 95
RWT8(3-F025)LBF | Fluorescent, (3) 48", HPT8 25W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 3 |  | 25 | 63 | 45 | 95
RWT8(3-F025)NBF | Fluorescent, (3) 48", HPT8 25W lamp, Instant or Program Start Ballast, (0.85 < BF < 0.95) | Electronic |  | 3 |  | 25 | 72 | 45 | 95
RWT8(3-F025)HBF | Fluorescent, (3) 48", HPT8 25W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 3 |  | 25 | 98 | 45 | 95
Intentionally Blank
HPT8(4-F032)LBF | Fluorescent, (4) 48", HPT8 32W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 4 |  | 32 | 95 | 45 | 95
HPT8(4-F032)NBF | Fluorescent, (4) 48", HPT8 32W lamp, Instant or Program Start Ballast, (0.85 < BF < 0.95) | Electronic |  | 4 |  | 32 | 108 | 45 | 95
HPT8(4-F032)HBF | Fluorescent, (4) 48", HPT8 32W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 4 |  | 32 | 144 | 45 | 95
RWT8(4-F028)LBF | Fluorescent, (4) 48", HPT8 28W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 4 |  | 28 | 84 | 45 | 95
RWT8(4-F028)NBF | Fluorescent, (4) 48", HPT8 28W lamp | Electronic |  | 4 |  | 28 | 95 | 45 | 95
RWT8(4-F028)HBF | Fluorescent, (4) 48", HPT8 28W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 4 |  | 28 | 127 | 45 | 95
RWT8(4-F025)LBF | Fluorescent, (4) 48", HPT8 25W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 4 |  | 25 | 84 | 45 | 95
RWT8(4-F025)NBF | Fluorescent, (4) 48", HPT8 25W lamp, Instant or Program Start Ballast, (0.85 < BF < 0.95) | Electronic |  | 4 |  | 25 | 95 | 45 | 95
RWT8(4-F025)HBF | Fluorescent, (4) 48", HPT8 25W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 4 |  | 25 | 127 | 45 | 95
Intentionally Blank
HPT8(6-F032)LBF | Fluorescent, (6) 48", HPT8 32W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 6 |  | 32 | 146 | 75 | 210
HPT8(6-F032)NBF | Fluorescent, (6) 48", HPT8 32W lamp | Electronic |  | 6 |  | 32 | 163 | 75 | 210
HPT8(6-F032)HBF | Fluorescent, (6) 48", HPT8 32W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 6 |  | 32 | 222 | 75 | 210
Intentionally Blank
HPT8(8-F032)LBF | Fluorescent, (8) 48", HPT8 32W lamp, Instant or Program Start Ballast, (< 0.85) | Electronic |  | 8 |  | 32 | 190 | 75 | 210
HPT8(8-F032)NBF | Fluorescent, (8) 48", HPT8 32W lamp | Electronic |  | 8 |  | 32 | 216 | 75 | 210
HPT8(8-F032)HBF | Fluorescent, (8) 48", HPT8 32W lamp, Instant or Program Start Ballast, (>/= 0.95) | Electronic |  | 8 |  | 32 | 288 | 75 | 210
FU | Fluor_U_Tubes
(Existing Fixture)
FU1EE | Fluorescent, (1) U-Tube, ES lamp | Mag-ES |  | 1 |  | 35 | 43 | 0 | 0 | 0
FU1ES | Fluorescent, (1) U-Tube, ES Lamp | Mag-STD |  | 1 |  | 34 | 43 | 0 | 0 | 0
FU1ILL | Fluorescent, (1) U-Tube, T-8 lamp, Instant Start ballast | Electronic |  | 1 |  | 32 | 31 | 0 | 0 | 0
FU1ILU | Fluorescent, (1) 6" spacing U-Tube, T-8 lamp, IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 1 |  | 32 | 29 | 0 | 0 | 0
FU1ILU-H | Fluorescent, (1) 6" spacing U-Tube, T-8 lamp, IS Ballast, HLO (.95 < BF < 1.1) | Prem. Elec. |  | 1 |  | 32 | 34 | 0 | 0 | 0
FU1LL | Fluorescent, (1) U-Tube, T-8 lamp | Electronic |  | 1 |  | 32 | 32 | 0 | 0 | 0
FU1LL-R | Fluorescent, (1) U-Tube, T-8 lamp, RLO (BF < 0.85) | Electronic |  | 1 |  | 31 | 27 | 0 | 0 | 0
FU1SE | Fluorescent, (1) U-Tube, STD lamp | Mag-ES |  | 1 |  | 40 | 43 | 0 | 0 | 0
FU1SS | Fluorescent, (1) U-Tube, ES Lamp | Mag-STD |  | 1 |  | 40 | 43 | 0 | 0 | 0
FU2SS | Fluorescent, (1) U-Tube, STD lamp, STD Mag Ballast | Mag-STD |  | 2 |  | 40 | 72 | 0 | 0 | 0
Intentionally Blank
FU2EE | Fluorescent, (2) U-Tube, ES lamps | Mag-ES |  | 2 |  | 35 | 72 | 0 | 0 | 0
FU2EL | Fluorescent (2) 48" U-bent ES lamps, Electronic ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 34 | 63 | 0 | 0 | 0
FU2ES | Fluorescent, (2) U-Tube, ES lamps | Mag-STD |  | 1 |  | 35 | 72 | 0 | 0 | 0
FU2ILL | Fluorescent, (2) U-Tube, T-8 lamps, Instant Start Ballast | Electronic |  | 2 |  | 32 | 59 | 0 | 0 | 0
FU2ILL/T4 | Fluorescent, (2) U-Tube, T-8 lamps, Instant Start Ballast, Tandem 4-lamp ballast | Electronic |  | 2 |  | 32 | 56 | 0 | 0 | 0
FU2ILL/T4-R | Fluorescent, (2) U-Tube, T-8 lamps, Instant Start Ballast, RLO, Tandem 4-lamp ballast | Electronic |  | 2 |  | 32 | 49 | 0 | 0 | 0
FU2ILL-H | Fluorescent, (2) U-Tube, T-8 lamps, Instant Start HLO Ballast | Electronic |  | 2 |  | 32 | 65 | 0 | 0 | 0
FU2ILL-R | Fluorescent, (2) U-Tube, T-8 lamps, Instant Start RLO Ballast | Electronic |  | 2 |  | 32 | 52 | 0 | 0 | 0
FU2ILU | Fluorescent, (2) 6" spacing U-Tube, T-8 lamps, IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 32 | 55 | 0 | 0 | 0
FU2ILU-R | Fluorescent, (2) 6" spacing U-Tube, T-8 lamps, IS Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 2 |  | 32 | 48 | 0 | 0 | 0
FU2ILU-V | Fluorescent, (2) 6" spacing U-Tube, T-8 lamps, IS Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 2 |  | 32 | 73 | 0 | 0 | 0
FU2LL | Fluorescent, (2) U-Tube, T-8 lamps | Electronic |  | 2 |  | 32 | 60 | 0 | 0 | 0
FU2LL/T2 | Fluorescent, (2) U-Tube, T-8 lamps, Tandem 4-lamp ballast | Electronic |  | 2 |  | 32 | 59 | 0 | 0 | 0
FU2LL-R | Fluorescent, (2) U-Tube, T-8 lamps, RLO (BF < 0.85) | Electronic |  | 2 |  | 31 | 54 | 0 | 0 | 0
FU2SE | Fluorescent, (2) U-Tube, STD lamps | Mag-ES |  | 2 |  | 40 | 72 | 0 | 0 | 0
FU2SL | Fluorescent (2) 48" U-bent Standard lamps, Electronic ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 40 | 63 | 0 | 0 | 0
Intentionally Blank
FU3EE | Fluorescent, (3) U-Tube, ES lamps | Mag-ES |  | 3 |  | 35 | 115 | 0 | 0 | 0
(Replacement Fixture)
FU2ILL | Fluorescent, (2) U-Tube, T-8 lamps, Instant Start Ballast | Electronic |  | 2 |  | 32 | 59 | 40 | 75 | 60
FU2ILL-H | Fluorescent, (2) U-Tube, T-8 lamps, Instant Start HLO Ballast | Electronic |  | 2 |  | 32 | 65 | 40 | 75 | 60
FU2ILL-R | Fluorescent, (2) U-Tube, T-8 lamps, Instant Start RLO Ballast | Electronic |  | 2 |  | 32 | 52 | 40 | 75 | 60
FU2ILU | Fluorescent, (2) 6" spacing U-Tube, T-8 lamps, IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. |  | 2 |  | 32 | 55 | 40 | 75 | 60
FU2ILU-R | Fluorescent, (2) 6" spacing U-Tube, T-8 lamps, IS Ballast, RLO (BF < 0.85) | Prem. Elec. |  | 2 |  | 32 | 48 | 40 | 75 | 60
FU2ILU-V | Fluorescent, (2) 6" spacing U-Tube, T-8 lamps, IS Ballast, VHLO (BF > 1.1) | Prem. Elec. |  | 2 |  | 32 | 73 | 40 | 75 | 60
FU2LL | Fluorescent, (2) U-Tube, T-8 lamps | Electronic |  | 2 |  | 32 | 60 | 40 | 75 | 60
FU2LL-R | Fluorescent, (2) U-Tube, T-8 lamps, RLO (BF < 0.85) | Electronic |  | 2 |  | 31 | 54 | 40 | 75 | 60
FU2SL | Fluorescent (2) 48" U-bent Standard lamps, Electronic ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 40 | 63 | 40 | 75 | 60
FT5 | Fluor_T5_Linear
(Existing Fixture - Non-T5)
F1.51SS | Fluorescent, (1) 18" T12 lamp | Mag-STD |  | 1 |  | 15 | 19 | 0 | 0 | 0
Intentionally Blank
F1.52SS | Fluorescent, (2) 18", T12 lamps | Mag-STD |  | 2 |  | 15 | 36 | 0 | 0 | 0
Intentionally Blank
F21HS | Fluorescent, (1) 24", HO lamp | Mag-STD |  | 1 |  | 35 | 62 | 0 | 0 | 0
F21SS | Fluorescent, (1) 24", STD lamp | Mag-STD |  | 1 |  | 20 | 25 | 0 | 0 | 0
Intentionally Blank
F22HS | Fluorescent, (2) 24", HO lamps | Mag-STD |  | 2 |  | 35 | 90 | 0 | 0 | 0
F22SS | Fluorescent, (2) 24", STD lamps | Mag-STD |  | 2 |  | 20 | 50 | 0 | 0 | 0
Intentionally Blank
F23SS | Fluorescent, (3) 24", STD lamps | Mag-STD |  | 3 |  | 20 | 71 | 0 | 0 | 0
Intentionally Blank
F24SS | Fluorescent, (4) 24", STD lamps | Mag-STD |  | 4 |  | 20 | 100 | 0 | 0 | 0
Intentionally Blank
F26SS/2 | Fluorescent, (6) 24", STD lamps, (2) ballasts | Mag-STD |  | 6 |  | 20 | 146 | 0 | 0 | 0
Intentionally Blank
F31EE/T2 | Fluorescent, (1) 36", ES lamp, Tandem 2-lamp ballast | Mag-ES |  | 1 |  | 25 | 33 | 0 | 0 | 0
F31EL | Fluorescent, (1) 36", ES lamp | Electronic |  | 1 |  | 25 | 26 | 0 | 0 | 0
F31ES | Fluorescent, (1) 36", ES lamp | Mag-STD |  | 1 |  | 25 | 42 | 0 | 0 | 0
F31ES/T2 | Fluorescent, (1) 36", ES lamp, Tandem 2-lamp ballast | Mag-STD |  | 1 |  | 25 | 33 | 0 | 0 | 0
F31SE/T2 | Fluorescent, (1) 36", STD lamp, Tandem 2-lamp ballast | Mag-ES |  | 1 |  | 30 | 37 | 0 | 0 | 0
F31SHS | Fluorescent, (1) 36", HO lamp | Mag-STD |  | 1 |  | 50 | 70 | 0 | 0 | 0
F31SL | Fluorescent, (1) 36", STD lamp | Electronic |  | 1 |  | 30 | 31 | 0 | 0 | 0
F31SS | Fluorescent, (1) 36", STD lamp | Mag-STD |  | 1 |  | 30 | 46 | 0 | 0 | 0
F31SS/T2 | Fluorescent, (1) 36", STD lamp, Tandem 2-lamp ballast | Mag-STD |  | 1 |  | 30 | 41 | 0 | 0 | 0
Intentionally Blank
F32EE | Fluorescent, (2) 36", ES lamps | Mag-ES |  | 2 |  | 25 | 66 | 0 | 0 | 0
F32EL | Fluorescent, (2) 36", ES lamps | Electronic |  | 2 |  | 25 | 50 | 0 | 0 | 0
F32EL/T4 | Fluorescent, (2) 36" ES lamps, Tandem 4-lamp ballast, NLO (0.85 < BF < 0.95) | Electronic |  | 2 |  | 25 | 50 | 0 | 0 | 0
F32ES | Fluorescent, (2) 36", ES lamps | Mag-STD |  | 2 |  | 25 | 73 | 0 | 0 | 0
F32SE | Fluorescent, (2) 36", STD lamps | Mag-ES |  | 2 |  | 30 | 74 | 0 | 0 | 0
F32SHS | Fluorescent, (2) 36", HO, lamps | Mag-STD |  | 2 |  | 50 | 114 | 0 | 0 | 0
F32SL | Fluorescent, (2) 36", STD lamps | Electronic |  | 2 |  | 30 | 58 | 0 | 0 | 0
F32SS | Fluorescent, (2) 36", STD lamps | Mag-STD |  | 2 |  | 30 | 75 | 0 | 0 | 0
Intentionally Blank
F33ES | Fluorescent, (3) 36", ES lamps | Mag-STD |  | 3 |  | 25 | 115 | 0 | 0 | 0
F33SE | Fluorescent, (3) 36", STD lamps, (1) STD ballast and (1) ES ballast | Mag-ES |  | 3 |  | 30 | 120 | 0 | 0 | 0
F33SS | Fluorescent, (3) 36", STD lamps | Mag-STD |  | 3 |  | 30 | 127 | 0 | 0 | 0
Intentionally Blank
F34EE | Fluorescent, (4) 36", ES lamps | Mag-ES |  | 4 |  | 25 | 132 | 0 | 0 | 0
F34SE | Fluorescent, (4) 36", STD lamps | Mag-ES |  | 4 |  | 30 | 148 | 0 | 0 | 0
F34SL | Fluorescent, (4) 36", STD lamps | Electronic |  | 4 |  | 30 | 116 | 0 | 0 | 0
F34SS | Fluorescent, (4) 36", STD lamps | Mag-STD |  | 4 |  | 30 | 150 | 0 | 0 | 0
Intentionally Blank
F36EE | Fluorescent, (6) 36", ES lamps | Mag-ES |  | 6 |  | 30 | 198 | 0 | 0 | 0
F36ES | Fluorescent, (6) 36", ES lamps | Mag-STD |  | 6 |  | 30 | 219 | 0 | 0 | 0
F36SE | Fluorescent, (6) 36", STD lamps | Mag-ES |  | 6 |  | 30 | 213 | 0 | 0 | 0
F36SS | Fluorescent, (6) 36", STD lamps | Mag-STD |  | 6 |  | 30 | 225 | 0 | 0 | 0
Intentionally Blank
F40SE/D1 | Fluorescent, (0) 48" lamps, Completely delamped fixture with (1) hot ballast | Mag-ES |  | 1 |  | 0 | 4 | 0 | 0 | 0
F40SE/D2 | Fluorescent, (0) 48" lamps, Completely delamped fixture with (2) hot ballast | Mag-ES |  | 1 |  | 0 | 8 | 0 | 0 | 0
Intentionally Blank
F41EE | Fluorescent, (1) 48", ES lamp | Mag-ES |  | 1 |  | 34 | 43 | 0 | 0 | 0
F41EE/D2 | Fluorescent, (1) 48", ES lamp, 2 ballast | Mag-ES |  | 1 |  | 34 | 43 | 0 | 0 | 0
F41EE/T2 | Fluorescent, (1) 48", ES lamp, Tandem 2-lamp ballast | Mag-ES |  | 1 |  | 34 | 36 | 0 | 0 | 0
F41EHS | Fluorescent, (1) 48", ES HO lamp | Mag-STD |  | 1 |  | 55 | 80 | 0 | 0 | 0
F41EIS | Fluorescent, (1) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD |  | 1 |  | 30 | 51 | 0 | 0 | 0
F41EL | Fluorescent, (1) 48", T12 ES lamp, Electronic Ballast | Electronic |  | 1 |  | 34 | 32 | 0 | 0 | 0
F41IAL | Fluorescent, (1) 48", F25T12 lamp, Instant Start Ballast | Electronic |  | 1 |  | 25 | 25 | 0 | 0 | 0
F41IAL/T2-R | Fluorescent, (1) 48", F25T12 lamp, Tandem 2-Lamp IS ballast, RLO (BF < 0.85) | Electronic |  | 1 |  | 25 | 19 | 0 | 0 | 0
F41IAL/T3-R | Fluorescent, (1) 48", F25T12 lamp, Tandem 3-Lamp IS ballast, RLO (BF < 0.85) | Electronic |  | 1 |  | 25 | 20 | 0 | 0 | 0
F41IAL/T4-R | Fluorescent, (1) 48", F25T12 lamp, Tandem 4-Lamp IS ballast, RLO (BF < 0.85) | Electronic |  | 1 |  | 25 | 20 | 0 | 0 | 0
F41SHS | Fluorescent, (1) 48", STD HO lamp | Mag-STD |  | 1 |  | 60 | 85 | 0 | 0 | 0
F41SIL | Fluorescent, (1) 48", STD IS lamp, Electronic ballast | Electronic |  | 1 |  | 39 | 46 | 0 | 0 | 0
F41SIL/T2 | Fluorescent, (1) 48", STD IS lamp, Tandem 2-lamp IS ballast | Electronic |  | 1 |  | 39 | 37 | 0 | 0 | 0
F41SVS | Fluorescent, (1) 48", STD VHO lamp | Mag-STD |  | 1 |  | 110 | 140 | 0 | 0 | 0
F41TS | Fluorescent, (1) 48", T-10 lamp | Mag-STD |  | 1 |  | 40 | 51 | 0 | 0 | 0
Intentionally Blank
F42EE | Fluorescent, (2) 48", ES lamp | Mag-ES |  | 2 |  | 34 | 72 | 0 | 0 | 0
F42EE/2 | Fluorescent, (2) 48", ES lamps, (2) 1-lamp ballasts | Mag-ES |  | 2 |  | 34 | 86 | 0 | 0 | 0
F42EE/D2 | Fluorescent, (2) 48", ES lamps, 2 Ballasts (delamped) | Mag-ES |  | 2 |  | 34 | 76 | 0 | 0 | 0
F42EHS | Fluorescent, (2) 42", HO lamps (3.5' lamp) | Mag-STD |  | 2 |  | 55 | 135 | 0 | 0 | 0
F42EIS | Fluorescent, (2) 48" ES Instant Start lamps. Magnetic ballast | Mag-STD |  | 2 |  | 30 | 82 | 0 | 0 | 0
F42EL | Fluorescent, (2) 48", T12 ES lamps, Electronic Ballast | Electronic |  | 2 |  | 34 | 60 | 0 | 0 | 0
F42IAL/T4-R | Fluorescent, (2) 48", F25T12 lamps, Tandem 4-lamp IS Ballast, RLO (BF < 0.85) | Electronic |  | 2 |  | 25 | 40 | 0 | 0 | 0
F42IAL-R | Fluorescent, (2) 48", F25T12 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 2 |  | 25 | 39 | 0 | 0 | 0
F42SHS | Fluorescent, (2) 48", STD HO lamps | Mag-STD |  | 2 |  | 60 | 145 | 0 | 0 | 0
F42SIL | Fluorescent, (2) 48", STD IS lamps, Electronic ballast | Electronic |  | 2 |  | 39 | 74 | 0 | 0 | 0
F42SVS | Fluorescent, (2) 48", STD VHO lamps | Mag-STD |  | 2 |  | 110 | 252 | 0 | 0 | 0
Intentionally Blank
F43EE | Fluorescent, (3) 48", ES lamps | Mag-ES |  | 3 |  | 34 | 115 | 0 | 0 | 0
F43EE/T2 | Fluorescent, (3) 48", ES lamps, Tandem 2-lamp ballasts | Mag-ES |  | 3 |  | 34 | 108 | 0 | 0 | 0
F43EHS | Fluorescent, (3) 42", HO lamps (3.5' lamp) | Mag-STD |  | 3 |  | 55 | 215 | 0 | 0 | 0
F43EIS | Fluorescent, (3) 48" ES Instant Start lamps. Magnetic ballast | Mag-STD |  | 3 |  | 30 | 133 | 0 | 0 | 0
F43EL | Fluorescent, (3) 48", T12 ES lamps, Electronic Ballast | Electronic |  | 3 |  | 34 | 92 | 0 | 0 | 0
F43IAL-R | Fluorescent, (3) 48", F25T12 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 3 |  | 25 | 60 | 0 | 0 | 0
F43SHS | Fluorescent, (3) 48", STD HO lamps | Mag-STD |  | 3 |  | 60 | 230 | 0 | 0 | 0
F43SIL | Fluorescent, (3) 48", STD IS lamps, Electronic ballast | Electronic |  | 3 |  | 39 | 120 | 0 | 0 | 0
F43SVS | Fluorescent, (3) 48", STD VHO lamps | Mag-STD |  | 3 |  | 110 | 377 | 0 | 0 | 0
Intentionally Blank
F44EE | Fluorescent, (4) 48", ES lamps | Mag-ES |  | 4 |  | 34 | 144 | 0 | 0 | 0
F44EE/D3 | Fluorescent, (4) 48", ES lamps, 3 Ballasts (delamped) | Mag-ES |  | 4 |  | 34 | 148 | 0 | 0 | 0
F44EE/D4 | Fluorescent, (4) 48", ES lamps, 4 Ballasts (delamped) | Mag-ES |  | 4 |  | 34 | 152 | 0 | 0 | 0
F44EHS | Fluorescent, (4) 48", ES HO lamps | Mag-STD |  | 4 |  | 55 | 270 | 0 | 0 | 0
F44EIS | Fluorescent, (4) 48" ES Instant Start lamps. Magnetic ballast | Mag-STD |  | 4 |  | 30 | 164 | 0 | 0 | 0
F44EL | Fluorescent, (4) 48", T12 ES lamps, Electronic Ballast | Electronic |  | 4 |  | 34 | 120 | 0 | 0 | 0
F44EVS | Fluorescent, (4) 48", VHO ES lamps | Mag-STD |  | 4 |  | 0 | 420 | 0 | 0 | 0
F44IAL-R | Fluorescent, (4) 48", F25T12 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic |  | 4 |  | 25 | 80 | 0 | 0 | 0
F44SHS | Fluorescent, (4) 48", STD HO lamps | Mag-STD |  | 4 |  | 60 | 290 | 0 | 0 | 0
F44SIL | Fluorescent, (4) 48", STD IS lamps, Electronic ballast | Electronic |  | 4 |  | 39 | 148 | 0 | 0 | 0
F44SVS | Fluorescent, (4) 48", STD VHO lamps | Mag-STD |  | 4 |  | 110 | 484 | 0 | 0 | 0
Intentionally Blank
F46EE | Fluorescent, (6) 48", ES lamps | Mag-ES |  | 6 |  | 34 | 216 | 0 | 0 | 0
F46EL | Fluorescent, (6) 48", ES lamps | Electronic |  | 6 |  | 34 | 180 | 0 | 0 | 0
F46SL | Fluorescent, (6) 48", STD lamps | Electronic |  | 6 |  | 40 | 186 | 0 | 0 | 0
Intentionally Blank
F48EE | Fluorescent, (8) 48", ES lamps | Mag-ES |  | 8 |  | 34 | 288 | 0 | 0 | 0
Intentionally Blank
F51SHE | Fluorescent, (1) 60", STD HO lamp | Mag-ES |  | 1 |  | 75 | 88 | 0 | 0 | 0
F51SHL | Fluorescent, (1) 60", STD HO lamp | Electronic |  | 1 |  | 75 | 69 | 0 | 0 | 0
F51SHS | Fluorescent, (1) 60", STD HO lamp | Mag-STD |  | 1 |  | 75 | 92 | 0 | 0 | 0
F51SL | Fluorescent, (1) 60", STD lamp | Electronic |  | 1 |  | 50 | 44 | 0 | 0 | 0
F51SS | Fluorescent, (1) 60", STD lamp | Mag-STD |  | 1 |  | 50 | 63 | 0 | 0 | 0
F51SVS | Fluorescent, (1) 60", VHO ES lamp | Mag-STD |  | 1 |  | 135 | 165 | 0 | 0 | 0
Intentionally Blank
F52SHE | Fluorescent, (2) 60", STD HO lamps | Mag-ES |  | 2 |  | 75 | 176 | 0 | 0 | 0
F52SHL | Fluorescent, (2) 60", STD HO lamps | Electronic |  | 2 |  | 75 | 138 | 0 | 0 | 0
F52SHS | Fluorescent, (2) 60", STD HO lamps | Mag-STD |  | 2 |  | 75 | 168 | 0 | 0 | 0
F52SL | Fluorescent, (2) 60", STD lamps | Electronic |  | 2 |  | 50 | 88 | 0 | 0 | 0
F52SS | Fluorescent, (2) 60", STD lamps | Mag-STD |  | 2 |  | 50 | 128 | 0 | 0 | 0
F52SVS | Fluorescent, (2) 60", VHO ES lamps | Mag-STD |  | 2 |  | 135 | 310 | 0 | 0 | 0
Intentionally Blank
F61ISL | Fluorescent, (1) 72", STD lamp, IS electronic ballast | Electronic |  | 1 |  | 55 | 68 | 0 | 0 | 0
F61SHS | Fluorescent, (1) 72", STD HO lamp | Mag-STD |  | 1 |  | 85 | 106 | 0 | 0 | 0
F61SS | Fluorescent, (1) 72", STD lamp | Mag-STD |  | 1 |  | 55 | 76 | 0 | 0 | 0
F61SVS | Fluorescent, (1) 72", VHO lamp | Mag-STD |  | 1 |  | 160 | 180 | 0 | 0 | 0
Intentionally Blank
F62ISL | Fluorescent, (2) 72", STD lamps, IS electronic ballast | Electronic |  | 2 |  | 55 | 108 | 0 | 0 | 0
F62SE | Fluorescent, (2) 72", STD lamps | Mag-ES |  | 2 |  | 55 | 122 | 0 | 0 | 0
F62SHE | Fluorescent, (2) 72", STD HO lamps | Mag-ES |  | 2 |  | 85 | 194 | 0 | 0 | 0
F62SHL | Fluorescent, (2) 72", STD HO lamps | Electronic |  | 2 |  | 85 | 167 | 0 | 0 | 0
F62SHS | Fluorescent, (2) 72", STD HO lamps | Mag-STD |  | 2 |  | 85 | 200 | 0 | 0 | 0
F62SL | Fluorescent, (2) 72", STD lamps | Electronic |  | 2 |  | 55 | 108 | 0 | 0 | 0
F62SS | Fluorescent, (2) 72", STD lamps | Mag-STD |  | 2 |  | 55 | 142 | 0 | 0 | 0
F62SVS | Fluorescent, (2) 72", VHO lamps | Mag-STD |  | 2 |  | 160 | 330 | 0 | 0 | 0
Intentionally Blank
F63ISL | Fluorescent, (3) 72", STD lamps, IS electronic ballast | Electronic |  | 3 |  | 55 | 176 | 0 | 0 | 0
F63SS | Fluorescent, (3) 72", STD lamps | Mag-STD |  | 3 |  | 55 | 202 | 0 | 0 | 0
Intentionally Blank
F64ISL | Fluorescent, (4) 72", STD lamps, IS electronic ballast | Electronic |  | 4 |  | 55 | 216 | 0 | 0 | 0
F64SE | Fluorescent, (4) 72", STD lamps | Mag-ES |  | 4 |  | 55 | 244 | 0 | 0 | 0
F64SHE | Fluorescent, (4) 72", HO lamps | Mag-ES |  | 4 |  | 85 | 388 | 0 | 0 | 0
F64SS | Fluorescent, (4) 72", STD lamps | Mag-STD |  | 4 |  | 56 | 244 | 0 | 0 | 0
Intentionally Blank
F81EE | Fluorescent, (1) 96" ES lamp | Mag-ES |  | 1 |  | 60 | 75 | 0 | 0 | 0
F81EE/T2 | Fluorescent, (1) 96", ES lamp, Tandem 2-lamp ballast | Mag-ES |  | 1 |  | 60 | 61.5 | 0 | 0 | 0
F81EHL | Fluorescent, (1) 96", ES HO lamp | Electronic |  | 1 |  | 95 | 80 | 0 | 0 | 0
F81EHS | Fluorescent, (1) 96", ES HO lamp | Mag-STD |  | 1 |  | 95 | 113 | 0 | 0 | 0
F81EL | Fluorescent, (1) 96", ES lamp | Electronic |  | 1 |  | 60 | 69 | 0 | 0 | 0
F81EL/T2 | Fluorescent, (1) 96", ES lamp, Tandem 2-lamp ballast | Electronic |  | 1 |  | 60 | 55 | 0 | 0 | 0
F81EVS | Fluorescent, (1) 96", ES VHO lamp | Mag-STD |  | 1 |  | 185 | 205 | 0 | 0 | 0
F81SGS | Fluorescent, (1) 96", T17 Grooved lamp | Mag-STD |  | 1 |  | 215 | 235 | 0 | 0 | 0
F81SHS | Fluorescent, (1) 96", STD HO lamp | Mag-STD |  | 1 |  | 110 | 121 | 0 | 0 | 0
F81SL | Fluorescent, (1) 96", STD lamp | Electronic |  | 1 |  | 75 | 69 | 0 | 0 | 0
F81SL/T2 | Fluorescent, (1) 96", STD lamp, Tandem 2-lamp ballast | Electronic |  | 1 |  | 75 | 55 | 0 | 0 | 0
F81SVS | Fluorescent, (1) 96", STD VHO lamp | Mag-STD |  | 1 |  | 215 | 205 | 0 | 0 | 0
Intentionally Blank
F82EE | Fluorescent, (2) 96", ES lamps | Mag-ES |  | 2 |  | 60 | 123 | 0 | 0 | 0
F82EHE | Fluorescent, (2) 96", ES HO lamps | Mag-ES |  | 2 |  | 95 | 207 | 0 | 0 | 0
F82EHL | Fluorescent, (2) 96", ES HO lamps | Electronic |  | 2 |  | 95 | 173 | 0 | 0 | 0
F82EHS | Fluorescent, (2) 96", ES HO lamps | Mag-STD |  | 2 |  | 95 | 207 | 0 | 0 | 0
F82EL | Fluorescent, (2) 96", ES lamps | Electronic |  | 2 |  | 60 | 110 | 0 | 0 | 0
F82EVS | Fluorescent, (2) 96", ES VHO lamps | Mag-STD |  | 2 |  | 195 | 380 | 0 | 0 | 0
F82SHE | Fluorescent, (2) 96", STD HO lamps | Mag-ES |  | 2 |  | 110 | 207 | 0 | 0 | 0
F82SHL | Fluorescent, (2) 96", STD HO lamps | Electronic |  | 2 |  | 110 | 173 | 0 | 0 | 0
F82SHS | Fluorescent, (2) 96", STD HO lamps | Mag-STD |  | 2 |  | 110 | 207 | 0 | 0 | 0
F82SL | Fluorescent, (2) 96", STD lamps | Electronic |  | 2 |  | 75 | 110 | 0 | 0 | 0
F82SVS | Fluorescent, (2) 96", STD VHO lamps | Mag-STD |  | 2 |  | 215 | 380 | 0 | 0 | 0
Intentionally Blank
F83EE | Fluorescent, (3) 96", ES lamps | Mag-ES |  | 3 |  | 60 | 198 | 0 | 0 | 0
F83EHE | Fluorescent, (3) 96", ES HO lamps, (1) 2-lamp ES Ballast and (1) 1-lamp STD Ballast | Mag-ES/STD |  | 3 |  | 95 | 319 | 0 | 0 | 0
F83EHS | Fluorescent, (3) 96", ES HO lamps | Mag-STD |  | 3 |  | 95 | 319 | 0 | 0 | 0
F83EL | Fluorescent, (3) 96", ES lamps | Electronic |  | 3 |  | 60 | 179 | 0 | 0 | 0
F83EVS | Fluorescent, (3) 96", ES VHO lamps | Mag-STD |  | 3 |  | 185 | 585 | 0 | 0 | 0
F83SHE | Fluorescent, (3) 96", STD HO lamps | Mag-ES |  | 3 |  | 110 | 319 | 0 | 0 | 0
F83SHS | Fluorescent, (3) 96", STD HO lamps | Mag-STD |  | 3 |  | 110 | 319 | 0 | 0 | 0
F83SL | Fluorescent, (3) 96", STD lamps | Electronic |  | 3 |  | 75 | 179 | 0 | 0 | 0
F83SVS | Fluorescent, (3) 96", STD VHO lamps | Mag-STD |  | 3 |  | 215 | 585 | 0 | 0 | 0
Intentionally Blank
F84EE | Fluorescent, (4) 96", ES lamps | Mag-ES |  | 4 |  | 60 | 246 | 0 | 0 | 0
F84EHE | Fluorescent, (4) 96", ES HO lamps | Mag-ES |  | 4 |  | 95 | 414 | 0 | 0 | 0
F84EHL | Fluorescent, (4) 96", ES HO lamps | Electronic |  | 4 |  | 95 | 346 | 0 | 0 | 0
F84EHS | Fluorescent, (4) 96", ES HO lamps | Mag-STD |  | 4 |  | 95 | 414 | 0 | 0 | 0
F84EL | Fluorescent, (4) 96", ES lamps | Electronic |  | 4 |  | 60 | 220 | 0 | 0 | 0
F84EVS | Fluorescent, (4) 96", ES VHO lamps | Mag-STD |  | 4 |  | 185 | 760 | 0 | 0 | 0
F84SHE | Fluorescent, (4) 96", STD HO lamps | Mag-ES |  | 4 |  | 110 | 414 | 0 | 0 | 0
F84SHL | Fluorescent, (4) 96", STD HO lamps | Electronic |  | 4 |  | 110 | 346 | 0 | 0 | 0
F84SHS | Fluorescent, (4) 96", STD HO lamps | Mag-STD |  | 4 |  | 110 | 414 | 0 | 0 | 0
F84SL | Fluorescent, (4) 96", STD lamps | Electronic |  | 4 |  | 75 | 220 | 0 | 0 | 0
F84SVS | Fluorescent, (4) 96", STD VHO lamps | Mag-STD |  | 4 |  | 215 | 760 | 0 | 0 | 0
Intentionally Blank
F86EE | Fluorescent, (6) 96", ES lamps | Mag-ES |  | 6 |  | 60 | 369 | 0 | 0 | 0
F86EHS | Fluorescent, (6) 96", ES HO lamps | Mag-STD |  | 6 |  | 95 | 519 | 0 | 0 | 0
Intentionally Blank
F88EHE | Fluorescent, (8) 96", ES HO lamps | Mag-ES |  | 8 |  | 95 | 828 | 0 | 0 | 0
F88SHS | Fluorescent, (8) 96", STD HO lamps | Mag-STD |  | 8 |  | 110 | 828 | 0 | 0 | 0
(Replacement Fixture)
F22PS | Fluorescent, (2) 21", Preheat T5 lamps, (1) Magnetic ballasts with integral starter, (BF=0.80) | Mag-STD |  | 2 |  | 13 | 26 | 40 | 75 | 60
Intentionally Blank
F24PS | Fluorescent, (4) 21", Preheat T5 lamps, (2) Magnetic ballasts with integral starter (BF=0.80) | Mag-STD |  | 4 |  | 13 | 53 | 40 | ? | 60
Intentionally Blank
F21GPHL-H | Fluorescent (1) 22" (563mm) T-5 HO lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 1 |  | 24 | 27 | 40 | 75
F21GPL-H | Fluorescent (1) 22" (563mm) T-5 lamp | PRS Elec. |  | 1 |  | 14 | 18 | 40 | 75
F22GPHL-H | Fluorescent (2) 22" (563mm) T-5 HO lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 2 |  | 24 | 52 | 40 | 75 | 60
F22GPL-H | Fluorescent (2) 22" (563mm) T-5 lamps | PRS Elec. |  | 2 |  | 14 | 33 | 40 | 75 | 60
Intentionally Blank
F23GPHL/2-H | Fluorescent (3) 22" (563mm)T-5 HO lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 3 |  | 24 | 79 | 40 | ?
F23GPL/2-H | Fluorescent (3) 22" (563mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 3 |  | 14 | 51 | 40 | 100
F23GPL-H | Fluorescent (3) 22" (563mm)T-5 lamps | PRS Elec. |  | 3 |  | 14 | 50 | 40 | 100
Intentionally Blank
F24GPHL/2-H | Fluorescent (4) 22" (563mm)T-5 HO lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 4 |  | 24 | 104 | 40 | 100 | 60
F24GPL/2-H | Fluorescent (4) 22" (563mm)T-5 lamps | PRS Elec. |  | 4 |  | 14 | 66 | 40 | 100 | 60
Intentionally Blank
F31GPHL-H | Fluorescent (1) 34" (863mm) T-5 HO lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 1 |  | 39 | 44 | 40 | 75
F31GPL-H | Fluorescent (1) 34" (863mm) T-5 lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 1 |  | 21 | 25 | 40 | 75
Intentionally Blank
F32GPHL-H | Fluorescent (2) 34" (863mm) T-5 HO lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 2 |  | 39 | 86 | 40 | 75 | 60
F32GPL-H | Fluorescent (2) 34" (863mm) T-5 lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 2 |  | 21 | 48 | 40 | 75 | 60
Intentionally Blank
F33GPHL/2-H | Fluorescent (3) 34" (863mm)T-5 HO lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 3 |  | 39 | 130 | 40 | 100
F33GPL/2-H | Fluorescent (3) 34" (863mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 3 |  | 21 | 73 | 40 | 100
Intentionally Blank
F34GPHL/2-H | Fluorescent (4) 34" (863mm)T-5 HO lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 4 |  | 39 | 172 | 40 | 100 | 60
F34GPL/2-H | Fluorescent (4) 34" (863mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 4 |  | 21 | 96 | 40 | 100 | 60
Intentionally Blank
F41GPHL/T2-H | Fluorescent (1) T-5 HO 45.8" lamp, Tandem 2-lamp PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 1 |  | 54 | 58.5 | 35 | 75
F41GPHL-H | Fluorescent (1) T-5 HO 45.8" lamps, Programmed Rapid Start, Electronic Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 1 |  | 54 | 62 | 35 | 75
F41GPL/T2-H | Fluorescent (1) 45.8" (1163mm) T-5 lamp; Tandem 2-lamp PRS Ballast,HLO (.95 < BF < 1.1) | PRS Elec. |  | 1 |  | 28 | 31.5 | 35 | 75
F41GPL-H | Fluorescent (1) 45.8" (1163mm) T-5 lamp | PRS Elec. |  | 1 |  | 28 | 33 | 35 | 75
Intentionally Blank
F42GPHL-H | Fluorescent (2) T-5 HO 45.8" lamps, Programmed Rapid Start, Electronic Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 2 |  | 54 | 117 | 35 | 75 | 60
F42GPL-H | Fluorescent (2) 45.8" (1163mm) T-5 lamps | PRS Elec. |  | 2 |  | 28 | 63 | 35 | 75 | 60
Intentionally Blank
F43GPHL/2-H | Fluorescent (3) T-5 HO 45.8" lamps, Programmed Rapid Start, (2) Electronic Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 3 |  | 54 | 179 | 45 | 95 | 60
F43GPHL-H | Fluorescent, (3) 45.8", T-5 high-output lamps, (1) Programmed Rapid Start Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 3 |  | 54 | 179 | 45 | 95 | 60
F43GPL/2-H | Fluorescent (3) 45.8" (1163mm)T-5 lamps | PRS Elec. |  | 3 |  | 28 | 96 | 45 | 95 | 60
Intentionally Blank
F44GPHL/2-H | Fluorescent (4) T-5 HO 45.8" lamps, Programmed Rapid Start, (2) Electronic Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 4 |  | 54 | 234 | 45 | 95 | 60
F44GPHL-H | Fluorescent, (4) 45.8", T-5 high-output lamps, (1) Programmed Rapid Start Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 4 |  | 54 | 234 | 45 | 95 | 60
F44GPL/2-H | Fluorescent (4) 45.8" (1163mm)T-5 lamps | PRS Elec. |  | 4 |  | 28 | 126 | 45 | 95 | 60
Intentionally Blank
F46GPHL/2-H | Fluorescent, (6) 45.8", T-5 high-output lamps, (2) Programmed Rapid Start Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 6 |  | 54 | 358 | 75 | 210 | 60
F46GPHL/3-H | Fluorescent, (6) 45.8", T-5 high-output lamps | PRS Elec. |  | 6 |  | 54 | 351 | 75 | 210 | 60
Intentionally Blank
F48GPHL/2-H | Fluorescent, (8) 45.8", T-5 high-output lamps | PRS Elec. |  | 8 |  | 54 | 468 | 75 | 210 | 60
Intentionally Blank
F410GPHL/5-H | Fluorescent, (10) 45.8", T-5 high-output lamps, (5) Programmed Rapid Start Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 10 |  | 54 | 585 | ? | 265
Intentionally Blank
F412GPHL/6-H | Fluorescent, (12) 45.8", T-5 high-output lamps, (6) Programmed Rapid Start Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 12 |  | 54 | 702 | ? | 265
Intentionally Blank
F51GPHL-H | Fluorescent (1) 57.6" (1463mm) T-5 HO lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 1 |  | 80 | 90 | ? | ?
F51GPL-H | Fluorescent (1) 57.6" (1463mm) T-5 lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 1 |  | 35 | 40 | ? | ?
Intentionally Blank
F52GPHL/2-H | Fluorescent (2) 57.6" (1463mm) T-5 HO lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 2 |  | 80 | 180 | ? | ?
F52GPL-H | Fluorescent (2) 57.6" (1463mm) T-5 lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. |  | 2 |  | 35 | 78 | ? | ?
Intentionally Blank
F53GPL/2-H | Fluorescent (3) 57.6" (1463mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 3 |  | 35 | 118 | ? | ?
Intentionally Blank
F54GPL/2-H | Fluorescent (4) 57.6" (1463mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. |  | 4 |  | 35 | 156 | ? | ?
LED | LED_Fixtures
(Existing Fixture) - Enter existing fixture data here - ballast, lamp, ballast Watts, lamp Watts
Exist_Freezer_Cooler | T12 (1) 48" Lamp Fluorescent Freezer/Cooler Lighting | - | 1 | 1 | 10 | 40 | 50 | 0 | 0 | 0
Exist_Freezer_Cooler | T8 (1) 48" Lamp Fluorescent Freezer/Cooler Lighting | - | 1 | 1 | 3 | 32 | 35 | 0 | 0 | 0
Exist_Freezer_Cooler | Existing Fluorescent Freezer/Cooler Lighting 3 | - | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Exist_Freezer_Cooler | Existing Fluorescent Freezer/Cooler Lighting 4 | - | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Exist_Freezer_Cooler | Existing Fluorescent Freezer/Cooler Lighting 5 | - | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
(Replacement Fixture) - Enter replacement fixture data here - ballast, lamp, ballast Watts, lamp Watts
LED_Freezer_Cooler | LED (1) 24" Lamp Reach-In Freezer or Cooler Lighting | - | 1 | 1 | 0 | 8 | 8 | 0 | 50 | 0
LED_Freezer_Cooler | LED (1) 48" Lamp Reach-In Freezer or Cooler Lighting | - | 1 | 1 | 0 | 16 | 16 | 0 | 50 | 0
LED_Freezer_Cooler | LED (1) 96" Lamp Reach-In Freezer or Cooler Lighting | - | 1 | 1 | 0 | 32 | 32 | 0 | 50 | 0
I | Incand_Standard
(Existing Fixture)
I15/1 | Incandescent, (1) 15W lamp | - | - | 1 | 0 | 15 | 15 | 0 | 0 | 0
I20/1 | Incandescent, (1) 20W lamp | - | - | 1 | 0 | 20 | 20 | 0 | 0 | 0
I25/1 | Incandescent, (1) 25W lamp | - | - | 1 | 0 | 25 | 25 | 0 | 0 | 0
I30/1 | Incandescent, (1) 30W lamp | - | - | 1 | 0 | 30 | 30 | 0 | 0 | 0
I40/1 | Incandescent, (1) 40W lamp | - | - | 1 | 0 | 40 | 40 | 0 | 0 | 0
I50/1 | Incandescent, (1) 50W lamp | - | - | 1 | 0 | 50 | 50 | 0 | 0 | 0
I60/1 | Incandescent, (1) 60W lamp | - | - | 1 | 0 | 60 | 60 | 0 | 0 | 0
I75/1 | Incandescent, (1) 75W lamp | - | - | 1 | 0 | 75 | 75 | 0 | 0 | 0
I80/1 | Incandescent, (1) 80W lamp | - | - | 1 | 0 | 80 | 80 | 0 | 0 | 0
I100/1 | Incandescent, (1) 100W lamp | - | - | 1 | 0 | 100 | 100 | 0 | 0 | 0
I120/1 | Incandescent, (1) 120W lamp | - | - | 1 | 0 | 120 | 120 | 0 | 0 | 0
I150/1 | Incandescent, (1) 150W lamp | - | - | 1 | 0 | 150 | 150 | 0 | 0 | 0
I170/1 | Incandescent, (1) 170W lamp | - | - | 1 | 0 | 170 | 170 | 0 | 0 | 0
I200/1 | Incandescent, (1) 200W lamp | - | - | 1 | 0 | 200 | 200 | 0 | 0 | 0
I250/1 | Incandescent, (1) 250W lamp | - | - | 1 | 0 | 250 | 250 | 0 | 0 | 0
I300/1 | Incandescent, (1) 300W lamp | - | - | 1 | 0 | 300 | 300 | 0 | 0 | 0
I400/1 | Incandescent, (1) 400W lamp | - | - | 1 | 0 | 400 | 400 | 0 | 0 | 0
I500/1 | Incandescent, (1) 500W lamp | - | - | 1 | 0 | 500 | 500 | 0 | 0 | 0
I750/1 | Incandescent, (1) 750W lamp | - | - | 1 | 0 | 750 | 750 | 0 | 0 | 0
I1000/1 | Incandescent, (1) 1000W lamp | - | - | 1 | 0 | 1000 | 1000 | 0 | 0 | 0
I1500/1 | Incandescent, (1) 1500W lamp | - | - | 1 | 0 | 1500 | 1500 | 0 | 0 | 0
I2000/1 | Incandescent, (1) 2000W lamp | - | - | 1 | 0 | 2000 | 2000 | 0 | 0 | 0
H | Incand_Halogen
(Existing Fixture)
H35/1 | Halogen Incandescent, (1) 35W lamp | - | - | 1 | - | 35 | 35 | 0 | 0 | 0
H50/1 | Halogen Incandescent, (1) 50W lamp | - | - | 1 | - | 50 | 50 | 0 | 0 | 0
HLV50/1 | Halogen, (1) Low Voltage 50W 50MR16 lamp | - | - | 1 | - | 50 | 60 | 0 | 0 | 0
H60/1 | Halogen Incandescent, (1) 60W lamp | - | - | 1 | - | 60 | 60 | 0 | 0 | 0
H75/1 | Halogen Incandescent, (1) 75W lamp | - | - | 1 | - | 75 | 75 | 0 | 0 | 0
H90/1 | Halogen Incandescent, (1) 90W lamp | - | - | 1 | - | 90 | 90 | 0 | 0 | 0
H100/1 | Halogen Incandescent, (1) 100W lamp | - | - | 1 | - | 100 | 100 | 0 | 0 | 0
H150/1 | Halogen Incandescent, (1) 150W lamp | - | - | 1 | - | 150 | 150 | 0 | 0 | 0
H250/1 | Halogen Incandescent, (1) 250W lamp | - | - | 1 | - | 250 | 250 | 0 | 0 | 0
H300/1 | Halogen Incandescent, (1) 300W lamp | - | - | 1 | - | 300 | 300 | 0 | 0 | 0
H500/1 | Halogen Incandescent, (1) 500W lamp | - | - | 1 | - | 500 | 500 | 0 | 0 | 0
CFL | CFL_Fixtures
(Replacement Fixture)
CFL1-13 | Interior CF (1) 13W | Electronic |  | 1 |  | 13 | 15 | 35 | 55 | 0
CFL2-13 | Interior CF (2) 13W | Electronic |  | 2 |  | 13 | 30 | 35 | 55 | 0
CFL3-13 | Interior CF (3) 13W | Electronic |  | 3 |  | 13 | 48 | 60 | 60 | 0
CFL1-23 | Interior CF (1) 23W | Electronic |  | 1 |  | 23 | 26 | 35 | 55 | 0
CFL1-26 | Interior CF (1) 26W | Electronic |  | 1 |  | 26 | 29 | 35 | 55 | 0
CFL2-26 | Interior CF (2) 26W | Electronic |  | 2 |  | 32 | 51 | 60 | 60 | 0
CFL1-32 | Interior CF (1) 32W | Electronic |  | 1 |  | 32 | 34 | 35 | 55 | 0
CFL2-32 | Interior CF (2) 32W | Electronic |  | 2 |  | 32 | 62 | 65 | 70 | 0
CFL1-42 | Interior CF (1) 42W | Electronic |  | 1 |  | 42 | 46 | 60 | 60 | 0
CFL2-42 | Interior CF (2) 42W | Electronic |  | 2 |  | 42 | 93 | 65 | 70 | 0
CFL1-57 | Interior CF (1) 57W | Electronic |  | 1 |  | 57 | 59 | 60 | 60 | 0
LED | LED_Fixtures
(Replacement Fixture) - Enter replacement fixture data here - ballast, lamp, ballast Watts, lamp Watts
LED_MR16 | MR 16 Integral LED Lamp | - | 0 | 1 | 0 | 8 | 8 | 0 | 40 | 0
LED_PAR20 | PAR 20 Integral LED Lamp | - | 0 | 1 | 0 | 10 | 10 | 0 | 50 | 0
LED_PAR38_PAR30 | PAR 38 (12W) Integral LED Lamp | - | 0 | 1 | 0 | 12 | 12 | 0 | 60 | 0
LED_PAR38_PAR30 | PAR 38 (13.5W) Integral LED Lamp | - | 0 | 1 | 0 | 13.5 | 13.5 | 0 | 60 | 0
LED_PAR38_PAR30 | PAR 30 (12W) Integral LED Lamp | - | 0 | 1 | 0 | 12 | 12 | 0 | 60 | 0
LED_RSORD_Fixture | Recessed, Surface, Pendant, or Track Head LED Fixture 10W | - | 0 | 1 | 0 | 10 | 10 | 0 | 35 | 0
LED_RSORD_Fixture | Recessed, Surface, Pendant, or Track Head LED Fixture 20W | - | 0 | 1 | 0 | 20 | 20 | 0 | 35 | 0
LED_RSORD_Fixture | Recessed, Surface, Pendant, or Track Head LED Fixture 30W | - | 0 | 1 | 0 | 30 | 30 | 0 | 35 | 0
LED_RSORD_Fixture | Recessed, Surface, Pendant, or Track Head LED Fixture 40W | - | 0 | 1 | 0 | 40 | 40 | 0 | 35 | 0
MH | Metal_Halide
(Existing Fixture)
MH100/1 | Metal Halide, (1) 100W lamp, Magnetic ballast | Magnetic | 1 | 1 | 27 | 100 | 127 | 0 | 0 | 0
MH125/1 | Metal Halide, (1) 125W lamp, Magnetic ballast | Magnetic | 1 | 1 | 25 | 125 | 150 | 0 | 0 | 0
MH150/1 | Metal Halide, (1) 150W lamp, Magnetic ballast | Magnetic | 1 | 1 | 34 | 150 | 184 | 0 | 0 | 0
MH175/1 | Metal Halide, (1) 175W lamp, Magnetic ballast | Magnetic | 1 | 1 | 34 | 175 | 209 | 0 | 0 | 0
MH200/1 | Metal Halide, (1) 200W lamp, Magnetic ballast | Magnetic | 1 | 1 | 32 | 200 | 232 | 0 | 0 | 0
MH250/1 | Metal Halide, (1) 250W lamp, Magnetic ballast | Magnetic | 1 | 1 | 41 | 250 | 291 | 0 | 0 | 0
MH320/1 | Metal Halide, (1) 320W lamp, Magnetic ballast | Magnetic | 1 | 1 | 47 | 320 | 367 | 0 | 0 | 0
MH350/1 | Metal Halide, (1) 350W lamp, Magnetic ballast | Magnetic | 1 | 1 | 45 | 350 | 395 | 0 | 0 | 0
MH360/1 | Metal Halide, (1) 360W lamp, Magnetic ballast | Magnetic | 1 | 1 | 58 | 360 | 418 | 0 | 0 | 0
MH400/1 | Metal Halide, (1) 400W lamp, Magnetic ballast | Magnetic | 1 | 1 | 56 | 400 | 456 | 0 | 0 | 0
MH450/1 | Metal Halide, (1) 450W lamp, Magnetic ballast | Magnetic | 1 | 1 | 57 | 450 | 507 | 0 | 0 | 0
MH750/1 | Metal Halide, (1) 750W lamp, Magnetic ballast | Magnetic | 1 | 1 | 64 | 750 | 814 | 0 | 0 | 0
MH1000/1 | Metal Halide, (1) 1000W lamp, Magnetic ballast | Magnetic | 1 | 1 | 77 | 1000 | 1077 | 0 | 0 | 0
MH1500/1 | Metal Halide, (1) 1500W lamp, Magnetic ballast | Magnetic | 1 | 1 | 108 | 1500 | 1608 | 0 | 0 | 0
MV | Mercury_Vapor
(Existing Fixture)
MV100/1 | Mercury Vapor, (1) 100W lamp | - | 1 | 1 | 25 | 100 | 125 | 0 | 0 | 0
MV160/1 | Mercury Vapor, Self-Ballasted, (1) 160W self-ballasted lamp | - | 1 | 1 | 0 | 160 | 160 | 0 | 0 | 0
MV175/1 | Mercury Vapor, (1) 175W lamp | - | 1 | 1 | 30 | 175 | 205 | 0 | 0 | 0
MV250/1 | Mercury Vapor, (1) 250W lamp | - | 1 | 1 | 40 | 250 | 290 | 0 | 0 | 0
MV400/1 | Mercury Vapor, (1) 400W lamp | - | 1 | 1 | 55 | 400 | 455 | 0 | 0 | 0
MV700/1 | Mercury Vapor, (1) 700W lamp | - | 1 | 1 | 80 | 700 | 780 | 0 | 0 | 0
MV1000/1 | Mercury Vapor, (1) 1000W lamp | - | 1 | 1 | 75 | 1000 | 1075 | 0 | 0 | 0
HPS | HP_Sodium
HPS100/1 | High Pressure Sodium, (1) 100W lamp |  |  | 1 |  | 100 | 138
HPS150/1 | High Pressure Sodium, (1) 150W lamp |  |  | 1 |  | 150 | 188
HPS200/1 | High Pressure Sodium, (1) 200W lamp |  |  | 1 |  | 200 | 250
HPS250/1 | High Pressure Sodium, (1) 250W lamp |  |  | 1 |  | 250 | 295
HPS310/1 | High Pressure Sodium, (1) 310W lamp |  |  | 1 |  | 310 | 365
HPS360/1 | High Pressure Sodium, (1) 360W lamp |  |  | 1 |  | 360 | 414
HPS400/1 | High Pressure Sodium, (1) 400W lamp |  |  | 1 |  | 400 | 465
HPS1000/1 | High Pressure Sodium, (1) 1000W lamp |  |  | 1 |  | 1000 | 1100
MH | Metal_Halide_Pulse_Start
(Replacement Fixture)
MHPS150/1 | Metal Halide Pulse Start, (1) 150w lamp | Magnetic | 1 | 1 | 35 | 150 | 185 | 210 | 115 | 0
MHPS175/1 | Metal Halide Pulse Start, (1) 175w lamp | Magnetic | 1 | 1 | 33 | 175 | 208 | 210 | 115 | 0
MHPS200/1 | Metal Halide Pulse Start, (1) 200w Lamp | Magnetic | 1 | 1 | 32 | 200 | 232 | 210 | 115 | 0
MHPS250/1 | Metal Halide Pulse Start, (1) 250w lamp | Magnetic | 1 | 1 | 38 | 250 | 288 | 210 | 115 | 0
MHPS320/1 | Metal Halide Pulse Start, (1) 320w lamp | Magnetic | 1 | 1 | 48 | 320 | 368 | 210 | 115 | 0
MHPS350/1 | Metal Halide Pulse Start, (1) 350W lamp | Magnetic | 1 | 1 | 50 | 350 | 400 | 210 | 115 | 0
MHPS400/1 | Metal Halide Pulse Start, (1) 400w lamp | Magnetic | 1 | 1 | 52 | 400 | 452 | 210 | 115 | 0
MHPS450/1 | Metal Halide Pulse Start, (1) 450w lamp | Magnetic | 1 | 1 | 58 | 450 | 508 | 210 | 115 | 0
LED | LED_Fixtures
(Replacement Fixture)
LED_RSORD_Fixture | Recessed, Surface, Pendant, or Track Head LED Fixture 10W | - | 0 | 1 | 0 | 10 | 10 | 0 | 35 | 0
LED_RSORD_Fixture | Recessed, Surface, Pendant, or Track Head LED Fixture 20W | - | 0 | 1 | 0 | 20 | 20 | 0 | 35 | 0
LED_RSORD_Fixture | Recessed, Surface, Pendant, or Track Head LED Fixture 30W | - | 0 | 1 | 0 | 30 | 30 | 0 | 35 | 0
LED_RSORD_Fixture | Recessed, Surface, Pendant, or Track Head LED Fixture 40W | - | 0 | 1 | 0 | 40 | 40 | 0 | 35 | 0
LED_ExtParkingGarage_GC | Parking Garage or Gas Station Canopy LED Fixture 35W | - | 0 | 1 |  | 35 | 35 | 0 | 250 | 0
LED_ExtParkingGarage_GC | Parking Garage or Gas Station Canopy LED Fixture 60W | - | 0 | 1 |  | 60 | 60 | 0 | 250 | 0
LED_ExtParkingGarage_GC | Parking Garage or Gas Station Canopy LED Fixture 80W | - | 0 | 1 |  | 80 | 80 | 0 | 250 | 0
LED_ExtParkingGarage_GC | Parking Garage or Gas Station Canopy LED Fixture 100W | - | 0 | 1 |  | 100 | 100 | 0 | 250 | 0
LED_ExtParkingGarage_GC | Parking Garage or Gas Station Canopy LED Fixture 150W | - | 0 | 1 |  | 150 | 150 | 0 | 250 | 0
LED_ExtParkingGarage_GC | Parking Garage or Gas Station Canopy LED Fixture 200W | - | 0 | 1 |  | 200 | 200 | 0 | 250 | 0
LED_ExtParkingLot_GC | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 35W | - | 0 | 1 |  | 35 | 35 | 0 | 115 | 0
LED_ExtParkingLot_GC | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 60W | - | 0 | 1 |  | 60 | 60 | 0 | 115 | 0
LED_ExtParkingLot_GC | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 80W | - | 0 | 1 |  | 80 | 80 | 0 | 115 | 0
LED_ExtParkingLot_GC | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 100W | - | 0 | 1 |  | 100 | 100 | 0 | 115 | 0
LED_ExtParkingLot_GC | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 150W | - | 0 | 1 |  | 150 | 150 | 0 | 115 | 0
LED_ExtParkingLot_GC | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 200W | - | 0 | 1 |  | 200 | 200 | 0 | 115 | 0
ECF | EXIT_Sign
(Existing Fixture)
ECF5/1 | EXIT Compact Fluorescent, (1) 5W lamp | Mag-STD | - | 1 | - | 5 | 9 | 0 | 0 | 0
ECF5/2 | EXIT Compact Fluorescent, (2) 5W lamps | Mag-STD | - | 2 | - | 5 | 20 | 0 | 0 | 0
ECF6/1 | EXIT Compact Fluorescent, (1) 6W lamp | Mag-STD | - | 1 | - | 6 | 13 | 0 | 0 | 0
ECF6/2 | EXIT Compact Fluorescent, (2) 6W lamps, (2) ballasts | Mag-STD | - | 2 | - | 6 | 26 | 0 | 0 | 0
ECF7/1 | EXIT Compact Fluorescent, (1) 7W lamp | Mag-STD | - | 1 | - | 7 | 10 | 0 | 0 | 0
ECF7/2 | EXIT Compact Fluorescent, (2) 7W lamps | Mag-STD | - | 2 | - | 7 | 21 | 0 | 0 | 0
ECF9/1 | EXIT Compact Fluorescent, (1) 9W lamp | Mag-STD | - | 1 | - | 9 | 12 | 0 | 0 | 0
ECF9/2 | EXIT Compact Fluorescent, (2) 9W lamps | Mag-STD | - | 2 | - | 9 | 20 | 0 | 0 | 0
EF2/2 | EXIT Sub-miniature T-1 Fluorescent, (2) lamps | Electronic | - | 2 | - | 2 | 5 | 0 | 0 | 0
EF6/1 | EXIT Miniature Bi-pin Fluorescent, (1) 6W lamp, (1) ballast | Mag-STD | - | 1 | - | 6 | 9 | 0 | 0 | 0
EF6/2 | EXIT Miniature Bi-pin Fluorescent, (2) 6W lamps, (2) ballasts | Mag-STD | - | 2 | - | 6 | 18 | 0 | 0 | 0
EF8/1 | EXIT T5 Fluorescent, (1) 8W lamp | Mag-STD | - | 1 | - | 8 | 12 | 0 | 0 | 0
EF8/2 | EXIT T5 Fluorescent, (2) 8W lamps | Mag-STD | - | 2 | - | 8 | 24 | 0 | 0 | 0
EI10/2 | EXIT Incandescent, (2) 10W lamps | - | - | 2 | - | 10 | 20 | 0 | 0 | 0
EI15/1 | EXIT Incandescent, (1) 15W lamp | - | - | 1 | - | 15 | 15 | 0 | 0 | 0
EI15/2 | EXIT Incandescent, (2) 15W lamps | - | - | 2 | - | 15 | 30 | 0 | 0 | 0
EI20/1 | EXIT Incandescent, (1) 20W lamp | - | - | 1 | - | 20 | 20 | 0 | 0 | 0
EI20/2 | EXIT Incandescent, (2) 20W lamps | - | - | 2 | - | 20 | 40 | 0 | 0 | 0
EI25/1 | EXIT Incandescent, (1) 25W lamp | - | - | 1 | - | 25 | 25 | 0 | 0 | 0
EI25/2 | EXIT Incandescent, (2) 25W lamps | - | - | 2 | - | 25 | 50 | 0 | 0 | 0
EI34/1 | EXIT Incandescent, (1) 34W lamp | - | - | 1 | - | 34 | 34 | 0 | 0 | 0
EI34/2 | EXIT Incandescent, (2) 34W lamps | - | - | 2 | - | 34 | 68 | 0 | 0 | 0
EI40/1 | EXIT Incandescent, (1) 40W lamp | - | - | 1 | - | 40 | 40 | 0 | 0 | 0
EI40/2 | EXIT Incandescent, (2) 40W lamps | - | - | 2 | - | 40 | 80 | 0 | 0 | 0
EI5/1 | EXIT Incandescent, (1) 5W lamp | - | - | 1 | - | 5 | 5 | 0 | 0 | 0
EI5/2 | EXIT Incandescent, (2) 5W lamps | - | - | 2 | - | 5 | 10 | 0 | 0 | 0
EI50/2 | EXIT Incandescent, (2) 50W lamps | - | - | 2 | - | 50 | 100 | 0 | 0 | 0
EI6/1 | EXIT Incandescent, (1) 6 W lamp | - | - | 1 | - | 6 | 6 | 0 | 0 | 0
EI6/2 | EXIT Incandescent, (2) 6 W lamps | - | - | 2 | - | 6 | 12 | 0 | 0 | 0
EI7.5/1 | EXIT Tungsten, (1) 7.5 W lamp | - | - | 1 | - | 7.5 | 8 | 0 | 0 | 0
EI7.5/2 | EXIT Tungsten, (2) 7.5 W lamps | - | - | 2 | - | 7.5 | 15 | 0 | 0 | 0
(Replacement Fixture)
ELED2/1 | EXIT Sign, LED, (1) 2W lamp, Single Sided | - | - | 1 | - | 2 | 6 | 35 | 35 | 0
ELED2/2 | EXIT Sign, LED, (2) 2W lamps, Dual Sided | - | - | 2 | - | 2 | 9 | 35 | 35 | 0
ELED3 | EXIT Sign, LED, 3W | - | - | 1 | - | 3 | 3 | 35 | 35 | 0
ELED4 | EXIT Sign, LED, 4W | - | - | 1 | - | 4 | 4 | 35 | 35 | 0
TS | Traffic_Signals
(Existing Fixture)
TS12RedC | 12" Red Circle | - | 1 | 1 | 0 | 100 | 100 | 0 | 0 | 0
TS12GreenC | 12" Green Circle | - | 1 | 1 | 0 | 100 | 100 | 0 | 0 | 0
TS8RedC | 8" Red Circle | - | 1 | 1 | 0 | 90 | 90 | 0 | 0 | 0
TS8GreenC | 8" Green Circle | - | 1 | 1 | 0 | 90 | 90 | 0 | 0 | 0
TSPedSig | Pedestrian Signal | - | 1 | 1 | 0 | 85 | 85 | 0 | 0 | 0
TS_LED | Rep_Traffic_Signals
(Replacement Fixture)
TS_LED12RedC | 12" Red Circle (LED) | - | 1 | 1 | 0 | 25 | 25 | 170 | 0 | 0
TS_LED12GreenC | 12" Green Circle (LED) | - | 1 | 1 | 0 | 25 | 25 | 170 | 0 | 0
TS_LED8RedC | 8" Red Circle (LED) | - | 1 | 1 | 0 | 15 | 15 | 0 | 0 | 0
TS_LED8GreenC | 8" Green Circle (LED) | - | 1 | 1 | 0 | 15 | 15 | 0 | 0 | 0
TS_LEDPedSig | Pedestrian Signal (LED) | - | 1 | 1 | 0 | 10 | 10 | 0 | 0 | 0
MISC | Miscellaneous_Fixtures
(Existing Fixture - Enter Fixture Data Here)
MIS_Ex1 | Old MIS1 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Ex2 | Old MIS2 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Ex3 | Old MIS3 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Ex4 | Old MIS4 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Ex5 | Old MIS5 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Ex6 | Old MIS6 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Ex7 | Old MIS7 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Ex8 | Old MIS8 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Ex9 | Old MIS9 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Ex10 | Old MIS10 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(Replacement Fixture - Enter Fixture Data Here)
MIS_Rep1 | New MIS1 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Rep2 | New MIS2 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Rep3 | New MIS3 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Rep4 | New MIS4 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Rep5 | New MIS5 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Rep6 | New MIS6 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Rep7 | New MIS7 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Rep8 | New MIS8 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Rep9 | New MIS9 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MIS_Rep10 | New MIS10 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Data light ECM (hidden)
Retrofit Table
Measure Code | Retrofit Description PEPCO measure description | Description as it Appears in Report (edit as necessary) NOTE: Each measure description must be unique - cannot share same name; If making differing recommendations for same measure type, enter on (2nd) line and/or insert line in that section and complete w/ appropriate data | Retro Type | Retrofit Fixture Choose recommendation for upgrade here | Cost of Retrofit | Rebate $ per Fixture
Incandescent Lighting
New Fixture Replacing Existing Fixture
LTN9 | New CFL Fixture <42W | Replace Existing Incandescent Fixture (<100W) w/ CFL Fixture | CFL | Interior CF (1) 23W | 68.75 | 55
LTN10 | New CFL Fixture > 42w to 60w | Replace Existing Incandescent Fixture (100-250W) w/ CFL Fixture | CFL | Interior CF (1) 32W | 75 | 60
LTN11 | New CFL Fixture > 60w | Replace Existing Incandescent Fixture (>250W) w/ CFL Fixture | CFL | Interior CF (2) 32W | 87.5 | 70
LTN12 | New CFL Fixture with Dimmable Ballast | Replace Existing Incandescent Fixture (<100W) w/ CFL Fixture with Dimmable Ballast | CFL | Interior CF (1) 23W | 100 | 80
LTN12 | New CFL Fixture with Dimmable Ballast | Replace Existing Incandescent Fixture (100-250W) w/ CFL Fixture with Dimmable Ballast | CFL | Interior CF (1) 32W | 100 | 80
LTN12 | New CFL Fixture with Dimmable Ballast | Replace Existing Incandescent Fixture (>250W) w/ CFL Fixture with Dimmable Ballast | CFL | Interior CF (2) 32W | 100 | 80
Relamp & Reballast of Existing Fixture
LTR6 | Retrofit CFL Fixture 42w or less | Retrofit Existing Incandescent Fixture (<100W) w/ CFL Fixture | CFL | Interior CF (1) 23W | 43.75 | 35
LTR7 | Retrofit CFL Fixture > 42w to 60w | Retrofit Existing Incandescent Fixture (100-250W) w/ CFL Fixture | CFL | Interior CF (1) 32W | 75 | 60
LTR8 | Retrofit CFL Fixture > 60w | Retrofit Existing Incandescent Fixture (>250W) w/ CFL Fixture | CFL | Interior CF (2) 32W | 81.25 | 65
LED Fixtures and Lamps
LTL1 | MR16 Integral LED Lamp | Replace Incandescent or CFL with MR16 Integral LED Lamp | LED | MR 16 Integral LED Lamp | 50 | 40
LTL2 | PAR38 and PAR30 Screw-in Integral LED Lamp | Replace Incandescent or CFL with PAR20 Screw-in Integral LED Lamp | LED | PAR 20 Integral LED Lamp | 62.5 | 50
LTL2 | PAR38 and PAR30 Screw-in Integral LED Lamp | Replace Incandescent or CFL with PAR38 Screw-in Integral LED Lamp | LED | PAR 38 (13.5W) Integral LED Lamp | 62.5 | 50
LTL2 | PAR38 and PAR30 Screw-in Integral LED Lamp | Replace Incandescent or CFL with PAR30 Screw-in Integral LED Lamp | LED | PAR 30 (12W) Integral LED Lamp | 62.5 | 50
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace >50W fixture with Pendant, Track, or Downlight LED Fixture (10W) | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 10W | 75 | 60
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace >70W fixture with Pendant, Track, or Downlight LED Fixture (20W) | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 20W | 85.7143 | 60
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace >90W fixture with Pendant, Track, or Downlight LED Fixture (30W) | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 30W | 100 | 60
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace >120W fixture with Pendant, Track, or Downlight LED Fixture (40W) | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 40W | 120 | 60
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >85W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (35W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 35W | 333.3333 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >120W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (60W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 60W | 375 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >160W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (80W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 80W | 428.5714 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >200W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (100W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 100W | 500 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >300W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (150W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 150W | 600 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >400W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (200W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 200W | 600 | 300
Linear Fluorescent Lamps and Fixtures |  |  | CFL/LED/T5T8/Misc
New Fixture Replacing Existing Fixture
LTN1 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (1 or 2, 4-ft Lamps and U-Bend Lamps) | Replace Existing (1) lamp 48" Fixture w/ HPT8 Lamps and Ballasts | T5T8 | Fluorescent, (1) 48", HPT8 28W lamp | 93.75 | 75
LTN1 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (1 or 2, 4-ft Lamps and U-Bend Lamps) | Replace Existing (1) lamp 48" Fixture w/ T5/T5HO Lamps and Ballasts | T5T8 | Fluorescent (1) 45.8" (1163mm) T-5 lamp | 93.75 | 75
LTN1 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (1 or 2, 4-ft Lamps and U-Bend Lamps) | Replace Existing (2) lamp 48" Fixture w/ HPT8 Lamps and Ballasts | T5T8 | Fluorescent, (2) 48", HPT8 28W lamp | 93.75 | 75
LTN1 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (1 or 2, 4-ft Lamps and U-Bend Lamps) | Replace Existing (2) lamp 48" Fixture w/ T5/T5HO Lamps and Ballasts | T5T8 | Fluorescent (2) 45.8" (1163mm) T-5 lamps | 93.75 | 75
LTN1 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (1 or 2, 4-ft Lamps and U-Bend Lamps) | Replace Existing (2) lamp U-Bend Fixture w/ T8 U-Bend Lamps and Ballasts | T5T8 | Fluorescent, (2) U-Tube, T-8 lamps | 93.75 | 75
LTN2 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (3 or 4, 4-ft Lamps) | Replace Existing (3) lamp 48" Fixture w/ HPT8 Lamps and Ballasts | T5T8 | Fluorescent, (3) 48", HPT8 28W lamp | 118.75 | 95
LTN2 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (3 or 4, 4-ft Lamps) | Replace Existing (3) lamp 48" Fixture w/ T5/T5HO Lamps and Ballasts | T5T8 | Fluorescent (3) 45.8" (1163mm)T-5 lamps | 118.75 | 95
LTN2 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (3 or 4, 4-ft Lamps) | Replace Existing (4) lamp 48" Fixture w/ HPT8 Lamps and Ballasts | T5T8 | Fluorescent, (4) 48", HPT8 28W lamp | 118.75 | 95
LTN2 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (3 or 4, 4-ft Lamps) | Replace Existing (4) lamp 48" Fixture w/ T5/T5HO Lamps and Ballasts | T5T8 | Fluorescent (4) 45.8" (1163mm)T-5 lamps | 118.75 | 95
LTN3 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (5 to 8, 4-ft Lamps) | Replace Existing (6) lamp 48" Fixture w/ HPT8 Lamps and Ballasts | T5T8 | Fluorescent, (6) 48", HPT8 32W lamp | 262.5 | 210
LTN3 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (5 to 8, 4-ft Lamps) | Replace Existing (6) lamp 48" Fixture w/ T5/T5HO Lamps and Ballasts | T5T8 | Fluorescent, (6) 45.8", T-5 high-output lamps | 262.5 | 210
LTN1 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (1 or 2, 4-ft Lamps and U-Bend Lamps) | Replace Existing (1) lamp 96" fixture w/ HPT8 Lamps and Ballasts | T5T8 | Fluorescent, (2) 48", HPT8 28W lamp | 93.75 | 75
LTN2 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (3 or 4, 4-ft Lamps) | Replace Existing (2) lamp 96" fixture w/ HPT8 Lamps and Ballasts | T5T8 | Fluorescent, (4) 48", HPT8 28W lamp | 118.75 | 95
LTN3 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (5 to 8, 4-ft Lamps) | Replace Existing (3) lamp 96" fixture w/ HPT8 Lamps and Ballasts | T5T8 | Fluorescent, (6) 48", HPT8 32W lamp | 262.5 | 210
LTN5 | New Fixture with T8 Lamps & HPT8 or RWT8 Ballasts, or T5/T5HO Lamps and Ballasts (1 or 2, 2-ft or 3-ft Lamps) | Replace Existing (1) lamp 24" Fixture w/ T5/T5HO lamps and Ballast | T5T8 | Fluorescent (1) 22" (563mm) T-5 lamp | 93.75 | 75
LTN5 | New Fixture with T8 Lamps & HPT8 or RWT8 Ballasts, or T5/T5HO Lamps and Ballasts (1 or 2, 2-ft or 3-ft Lamps) | Replace Existing (2) lamp 24" Fixture w/ T5/T5HO lamps and Ballast | T5T8 | Fluorescent (2) 22" (563mm) T-5 lamps | 93.75 | 75
LTN6 | New Fixture with T8 Lamps & HPT8 or RWT8 Ballasts, or T5/T5HO Lamps and Ballasts (3 or 4, 2-ft and 3-ft Lamps) | Replace Existing (3) lamp 24" Fixture w/ T5/T5HO lamps and Ballast | T5T8 | Fluorescent (3) 22" (563mm)T-5 lamps | 125 | 100
LTN6 | New Fixture with T8 Lamps & HPT8 or RWT8 Ballasts, or T5/T5HO Lamps and Ballasts (3 or 4, 2-ft and 3-ft Lamps) | Replace Existing (4) lamp 24" Fixture w/ T5/T5HO lamps and Ballast | T5T8 | Fluorescent (4) 22" (563mm)T-5 lamps | 125 | 100
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace with Pendant, Track, or Downlight LED Fixture 10W | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 10W | 75 | 60
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace with Pendant, Track, or Downlight LED Fixture 20W | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 20W | 85.7143 | 60
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace with Pendant, Track, or Downlight LED Fixture 30W | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 30W | 100 | 60
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace with Pendant, Track, or Downlight LED Fixture 40W | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 40W | 120 | 60
Relamp & Reballast of Existing Fixture
LTR1 | Relamp & Reballast with HPT8, RWT8, or T5/T5HO Lamps & Ballasts (Existing 1 & 2, 4-ft Lamp and U-Bend Lamp Fixtures) | Relamp & Reballast (1) lamp 48" Fixture w/ HPT8 & Ballast | T5T8 | Fluorescent, (1) 48", HPT8 28W lamp | 43.75 | 35
LTR1 | Relamp & Reballast with HPT8, RWT8, or T5/T5HO Lamps & Ballasts (Existing 1 & 2, 4-ft Lamp and U-Bend Lamp Fixtures) | Relamp & Reballast (2) lamp 48" Fixture w/ HPT8 & Ballast | T5T8 | Fluorescent, (2) 48", HPT8 28W lamp | 43.75 | 35
LTR1 | Relamp & Reballast with HPT8, RWT8, or T5/T5HO Lamps & Ballasts (Existing 1 & 2, 4-ft Lamp and U-Bend Lamp Fixtures) | Relamp & Reballast (2) lamp U-Bend Fixture w/ HPT8 & Ballast | T5T8 | Fluorescent, (2) U-Tube, T-8 lamps, Instant Start Ballast | 43.75 | 35
LTR2 | Relamp & Reballast with HPT8, RWT8, or T5/T5HO Lamps and Ballasts (Existing 3 & 4 Lamp 4-ft Fixtures) | Relamp & Reballast (3) lamp 48" Fixture w/ HPT8 & Ballast | T5T8 | Fluorescent, (3) 48", HPT8 28W lamp | 56.25 | 45
LTR2 | Relamp & Reballast with HPT8, RWT8, or T5/T5HO Lamps and Ballasts (Existing 3 & 4 Lamp 4-ft Fixtures) | Relamp & Reballast (4) lamp 48" Fixture w/ HPT8 & Ballast | T5T8 | Fluorescent, (4) 48", HPT8 28W lamp | 56.25 | 45
LTR3 | Relamp & Reballast with HPT8, RWT8, or T5/T5HO Lamps and Ballasts (Existing 5 to 8 Lamp 4-ft Fixtures) | Relamp & Reballast (6) lamp 48" Fixture w/ HPT8 & Ballast | T5T8 | Fluorescent, (6) 48", HPT8 32W lamp | 93.75 | 75
LTR3 | Relamp & Reballast with HPT8, RWT8, or T5/T5HO Lamps and Ballasts (Existing 5 to 8 Lamp 4-ft Fixtures) | Relamp & Reballast (8) lamp 48" Fixture w/ HPT8 & Ballast | T5T8 | Fluorescent, (8) 48", HPT8 32W lamp | 93.75 | 75
LTR4 | Relamp & Reballast with T8 Lamps and HPT8 or RWT8 Ballasts, or T5/T5HO Lamps and Ballasts (Existing 1 & 2 Lamp 2-ft and 3-ft Fixtures, including those with U-Bend Lamps) | Relamp & Reballast (1) lamp 24" Fixtures w/ HPT8 & Ballast | T5T8 | Fluorescent, (1) 24", T-8 lamp | 50 | 40
LTR4 | Relamp & Reballast with T8 Lamps and HPT8 or RWT8 Ballasts, or T5/T5HO Lamps and Ballasts (Existing 1 & 2 Lamp 2-ft and 3-ft Fixtures, including those with U-Bend Lamps) | Relamp & Reballast (2) lamp 24" Fixtures w/ HPT8 & Ballast | T5T8 | Fluorescent, (2) 24", T-8 lamps | 50 | 40
LTR5 | Relamp & Reballast with T8 Lamps and HPT8 or RWT8 Ballasts, or T5/T5HO Lamps and Ballasts (Existing 3 & 4 Lamp, 2-ft and 3-ft Fixtures) | Relamp & Reballast (3) lamp 24" Fixtures w/ HPT8 & Ballast | T5T8 | Fluorescent, (3) 24", T-8 lamps | 50 | 40
LTR5 | Relamp & Reballast with T8 Lamps and HPT8 or RWT8 Ballasts, or T5/T5HO Lamps and Ballasts (Existing 3 & 4 Lamp, 2-ft and 3-ft Fixtures) | Relamp & Reballast (4) lamp 24" Fixtures w/ HPT8 & Ballast | T5T8 | Fluorescent, (4) 24", T-8 lamps | 50 | 40
De-lamp/Retrofit of Existing Fixture
LTD1 | De-lamp/Retrofit with HPT8, RWT8, or T5/T5HO 4-ft Lamps and Ballasts and Retrofit Kit (Existing 4-ft and 8-ft fixtures with 2, 4-ft lamps or 1 or 2, 8-ft Lamps) | De-lamp/Retrofit 4ft. Fixture w/ HPT8 Lamps & Ballast | T5T8 | Fluorescent, (1) 48", HPT8 28W lamp | 75 | 60
LTD1 | De-lamp/Retrofit with HPT8, RWT8, or T5/T5HO 4-ft Lamps and Ballasts and Retrofit Kit (Existing 4-ft and 8-ft fixtures with 2, 4-ft lamps or 1 or 2, 8-ft Lamps) | De-lamp/Retrofit 4ft. Fixture w/ T5 Lamps & Ballast | T5T8 | Fluorescent (2) 45.8" (1163mm) T-5 lamps | 75 | 60
LTD2 | De-lamp/Retrofit with HPT8, RWT8, or T5/T5HO 4-ft Lamps and Ballasts and Retrofit Kit (Existing 4-ft and 8-ft fixtures with 3 or 4, 4-ft or 8-ft Lamps) | De-lamp/Retrofit 3 or 4 lamp 4ft. Fixture w/ HPT8 Lamps & Ballast | T5T8 | Fluorescent, (3) 48", HPT8 28W lamp | 75 | 60
LTD3 | De-lamp/Retrofit with HPT8, RWT8, or T5/T5HO Lamps and Ballasts and Retrofit Kit (Existing 5 to 8 Lamp, 4-ft Fixtures) | De-lamp/Retrofit 5 to 8 lamp 4ft. Fixture w/ HPT8 Lamps & Ballast | T5T8 | Fluorescent, (4) 48", HPT8 28W lamp | 93.75 | 75
LTD4 | De-lamp/Retrofit with T8 Lamps and HP Ballasts and Retrofit Kit (Existing 2 & 4 Lamp, 2-ft and 3-ft Fixtures) | De-lamp/Retrofit 2 or 4 lamp 2ft & 3ft. Fixture w/ T8 Lamps & HP Ballasts | T5T8 | Fluorescent, (2) 24", T-8 lamps | 75 | 60
LTD4 | De-lamp/Retrofit with T8 Lamps and HP Ballasts and Retrofit Kit (Existing 2 & 4 Lamp, 2-ft and 3-ft Fixtures, including those w/ U-Ben Lamps) | De-lamp/Retrofit 2 and 4 lamp 2ft or 3ft U-Bend fixtures | T5T8 | Fluorescent, (2) U-Tube, T-8 lamps | 75 | 60
Compact Fluorescent
New Fixture Replacing Existing Fixture
LTN9 | New CFL Fixture | Replace Existing Fixture w/ New CFL Fixture (<42W) | CFL | Interior CF (1) 13W | 68.75 | 55
LTN10 | New CFL Fixture > 42w to 60w | Replace Existing Incadescent Fixture w/ New CFL Fixture (42w to 60w) | CFL | Interior CF (2) 13W | 75 | 60
LTN11 | New CFL Fixture > 60w | Replace Existing Incadescent Fixture w/ New CFL Fixture (>60w) | CFL | Interior CF (1) 32W | 87.5 | 70
LTN12 | New CFL Fixture with Dimmable Ballast | Replace Existing Fixture w/ New CFL Fixture with Dimmable Ballast | CFL | Interior CF (1) 26W | 100 | 80
Relamp & Reballast of Existing Fixture
LTR6 | Retrofit CFL Fixture 42w or less | Retrofit Existing Fixture w/ New CFL Fixture | CFL | Interior CF (1) 13W | 43.75 | 35
LTR7 | Retrofit CFL Fixture > 42w to 60w | Retrofit Existing Incadescent Fixture w/ New CFL Fixture (>42w to 60w) | CFL | Interior CF (2) 13W | 75 | 60
LTR8 | Retrofit CFL Fixture > 60w | Retrofit Existing Incadescent Fixture w/ New CFL Fixture (>60w) | CFL | Interior CF (1) 32W | 43.75 | 35
LED Fixtures and Lamps
LTL1 | MR16 Integral LED Lamp | Replace Incandescent or CFL with MR16 Integral LED Lamp | LED | MR 16 Integral LED Lamp | 50 | 40
LTL2 | PAR38 and PAR30 Screw-in Integral LED Lamp | Replace Incandescent or CFL with PAR20 Screw-in Integral LED Lamp | LED | PAR 20 Integral LED Lamp | 62.5 | 50
LTL2 | PAR38 and PAR30 Screw-in Integral LED Lamp | Replace Incandescent or CFL with PAR38 Screw-in Integral LED Lamp | LED | PAR 38 (13.5W) Integral LED Lamp | 62.5 | 50
LTL2 | PAR38 and PAR30 Screw-in Integral LED Lamp | Replace Incandescent or CFL with PAR30 Screw-in Integral LED Lamp | LED | PAR 30 (12W) Integral LED Lamp | 62.5 | 50
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace with Pendant, Track, or Downlight LED Fixture 10W | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 10W | 75 | 60
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace with Pendant, Track, or Downlight LED Fixture 20W | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 20W | 75 | 60
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace with Pendant, Track, or Downlight LED Fixture 30W | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 30W | 75 | 60
LTL3 | Recessed, Surface, Pendant, Track, or Downlight LED Fixture | Replace with Pendant, Track, or Downlight LED Fixture 40W | LED | Recessed, Surface, Pendant, or Track Head LED Fixture 40W | 75 | 60
High Intensity Discharge, Exterior Parking Garage, Gasoline Canopy,Pole Lighting, Area Fixtures, and Wall Packs
New Fixture Replacing Existing Fixture
LTH1 | New Pulse Start Metal Halide Fixture (> / = 150 Watts) | Replace Existing 200W HID Fixture w/ 150W Pulse Start Metal Halide Fixture | Misc | Metal Halide Pulse Start, (1) 150w lamp | 262.5 | 210
LTH1 | New Pulse Start Metal Halide Fixture (> / = 150 Watts) | Replace Exisiting 250W HID Fixture w/ 200W Pulse Start Metal Halide Fixture | Misc | Metal Halide Pulse Start, (1) 200w Lamp | 262.5 | 210
LTH1 | New Pulse Start Metal Halide Fixture (> / = 150 Watts) | Replace Exisiting 300W HID Fixture w/ 250W Pulse Start Metal Halide Fixture | Misc | Metal Halide Pulse Start, (1) 250w lamp | 262.5 | 210
LTH1 | New Pulse Start Metal Halide Fixture (> / = 150 Watts) | Replace Exisiting 400W HID Fixture w/ 320W Pulse Start Metal Halide Fixture | Misc | Metal Halide Pulse Start, (1) 320w lamp | 262.5 | 210
LTH1 | New Pulse Start Metal Halide Fixture (> / = 150 Watts) | Replace Exisiting 500W HID Fixture w/ 400W Pulse Start Metal Halide Fixture | Misc | Metal Halide Pulse Start, (1) 400w lamp | 262.5 | 210
Relamp & Reballast of Existing Fixture
LTH2 | Probe-Start to Pulse-Start Metal Halide > or = 150W | Convert fixture from 200W Probe-start to 150W Pulse-Start Metal Halide | Misc | Metal Halide Pulse Start, (1) 150w lamp | 143.75 | 115 | 562.5
LTH2 | Probe-Start to Pulse-Start Metal Halide > or = 150W | Convert fixture from 250W Probe-start to 200W Pulse-Start Metal Halide | Misc | Metal Halide Pulse Start, (1) 200w Lamp | 143.75 | 115
LTH2 | Probe-Start to Pulse-Start Metal Halide > or = 150W | Convert fixture from 300W Probe-start to 250W Pulse-Start Metal Halide | Misc | Metal Halide Pulse Start, (1) 250w lamp | 143.75 | 115
LTH2 | Probe-Start to Pulse-Start Metal Halide > or = 150W | Convert fixture from 400W Probe-start to 320W Pulse-Start Metal Halide | Misc | Metal Halide Pulse Start, (1) 320w lamp | 143.75 | 115
LTH2 | Probe-Start to Pulse-Start Metal Halide > or = 150W | Convert fixture from 500W Probe-start to 400W Pulse-Start Metal Halide | Misc | Metal Halide Pulse Start, (1) 400w lamp | 143.75 | 115
T8T5 Replacements
LTN1 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (1 or 2, 4-ft Lamps and U-Bend Lamps) | Replace Existing 200-350W MH w/ 2 lamp 45.8" T5 | T5T8 | Fluorescent (2) 45.8" (1163mm) T-5 lamps | 93.75 | 75
LTN2 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (3 or 4, 4-ft Lamps) | Replace Existing 200-350W MH w/ 4 lamp 48" HPT8 | T5T8 | Fluorescent, (4) 48", HPT8 28W lamp | 118.75 | 95
LTN2 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (3 or 4, 4-ft Lamps) | Replace Existing 350-500W MH w/ 4 lamp 45.8" T5 | T5T8 | Fluorescent (4) 45.8" (1163mm)T-5 lamps | 118.75 | 95
LTN2 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (5 to 8, 4-ft Lamps) | Replace Existing 350-500W MH w/ 6 lamp 48" HPT8 | T5T8 | Fluorescent, (6) 48", HPT8 32W lamp | 262.5 | 210
LTN3 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (5 to 8, 4-ft Lamps) | Replace Existing 500-800W MH w/ 6 lamp 45.8" T5 | T5T8 | Fluorescent, (6) 45.8", T-5 high-output lamps | 262.5 | 210
LTN3 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (5 to 8, 4-ft Lamps) | Replace Existing 500-800W MH w/ 8 lamp48" HPT8 | T5T8 | Fluorescent, (8) 48", HPT8 32W lamp | 262.5 | 210
LTN3 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (5 to 8, 4-ft Lamps) | Replace Existing 800-1200W MH w/ 8 lamp 45.8" T5 | T5T8 | Fluorescent, (8) 45.8", T-5 high-output lamps | 262.5 | 210
LTN3 | New Fixture with HPT8, RWT8, or T5/T5HO Lamps and Ballasts, (5 to 8, 4-ft Lamps) | Replace Existing 800-1200W MH w/ 8 lamp 48" HPT8 | T5T8 | Fluorescent, (8) 48", HPT8 32W lamp | 262.5 | 210
LED Fixtures and Lamps
LTL5 | Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (>xxW Replaced) | >85W Replace with Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (35W) | LED | Parking Garage or Gas Station Canopy LED Fixture 35W | 511.1111 | 460
LTL5 | Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (>xxW Replaced) | >120W Replace with Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (60W) | LED | Parking Garage or Gas Station Canopy LED Fixture 60W | 575 | 460
LTL5 | Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (>xxW Replaced) | >160W Replace with Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (80W) | LED | Parking Garage or Gas Station Canopy LED Fixture 80W | 657.1429 | 460
LTL5 | Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (>xxW Replaced) | >200W Replace with Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (100W) | LED | Parking Garage or Gas Station Canopy LED Fixture 100W | 766.6667 | 460
LTL5 | Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (>xxW Replaced) | >300W Replace with Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (150W) | LED | Parking Garage or Gas Station Canopy LED Fixture 150W | 920 | 460
LTL5 | Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (>xxW Replaced) | >400W Replace with Exterior Parking Garage, Gasoline Canopy, or Pole Mounted LED Fixture (200W) | LED | Parking Garage or Gas Station Canopy LED Fixture 200W | 920 | 460
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >85W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (35W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 35W | 333.3333 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >120W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (60W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 60W | 375 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >160W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (80W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 80W | 428.5714 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >200W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (100W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 100W | 500 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >300W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (150W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 150W | 600 | 300
LTL6 | Exterior Parking Lot, area fixtures and wallpack LED fixtures (>xxW Replaced) | >400W Replace with Exterior Parking Lot, area fixtures or wallpack LED fixtures (200W) | LED | Parking Lot / Area Pole-Mounted and Wallpacks LED fixtures 200W | 600 | 300
Exit Signs
New Fixture Replacing Existing Fixture
LTL4 | New LED Exit Sign | Replace Existing Exit Sign w/ LED Exit Sign | LED | EXIT Sign, LED, (1) 2W lamp, Single Sided | 43.75 | 35
LTL4 | New LED Exit Sign | Replace Existing 2 sided Exit Sign w/ LED Exit Sign | LED | EXIT Sign, LED, (2) 2W lamps, Dual Sided | 43.75 | 35
LTL4 | New LED Exit Sign | Replace Existing CFL Exit Sign w/ LED Exit Sign | LED | EXIT Sign, LED, 3W | 43.75 | 35
LTL4 | New LED Exit Sign | Replace Existing IncanescentExit Sign w/ LED Exit Sign | LED | EXIT Sign, LED, 4W | 43.75 | 35
LTL4 | New LED Exit Sign | Replace Existing 2 sided Incandescent Exit Sign w/ LED Exit Sign | LED | EXIT Sign, LED, (2) 2W lamps, Dual Sided | 43.75 | 35
Traffic Signals
Relamp & Reballast of Existing Fixture
LTL8 | Retrofit 8-in. Traffic Signals to LED | Retrofit 8-in. Traffic Signal to LED | LED | 8" Red Circle (LED) | 62.5 | 50
LTL9 | Retrofit 12-in. Traffic Signals to LED | Retrofit 12-in. Traffic Signal to LED | LED | 12" Red Circle (LED) | 212.5 | 170
Reach-in Freezer or Cooler Lighting
LED Fixtures and Lamps
LTL7 | LED Reach-in Freezer or Cooler Lighting | Replace exisitng Reach-Freezer or Cooler Lighting w/ LED 24" Strip | LED | LED (1) 24" Lamp Reach-In Freezer or Cooler Lighting | 55.5556 | 50
LTL7 | LED Reach-in Freezer or Cooler Lighting | Replace exisitng Reach-Freezer or Cooler Lighting w/ LED 48" Strip | LED | LED (1) 48" Lamp Reach-In Freezer or Cooler Lighting | 62.5 | 50
LTL7 | LED Reach-in Freezer or Cooler Lighting | Replace exisitng Reach-Freezer or Cooler Lighting w/ LED 96" Strip | LED | LED (1) 96" Lamp Reach-In Freezer or Cooler Lighting | 71.4286 | 50
Miscellaneous | [5 empty] | Rebate $ per Fixture
LTA | MIS1 - Enter lighting Wattage and ballast information on 'Data light kwh' page | Replace Old MIS1 w/ New MIS1 |  | New MIS1 | 1.25 | 1
LTA | MIS2 - Enter lighting Wattage and ballast information on 'Data light kwh' page | Replace Old MIS2 w/ New MIS2 |  | New MIS2 | 1.25 | 1
LTA | MIS3 - Enter lighting Wattage and ballast information on 'Data light kwh' page | Replace Old MIS3 w/ New MIS3 |  | New MIS3 | 1.25 | 1
LTA | MIS4 - Enter lighting Wattage and ballast information on 'Data light kwh' page | Replace Old MIS4 w/ New MIS4 |  | New MIS4 | 1.25 | 1
LTA | MIS5 - Enter lighting Wattage and ballast information on 'Data light kwh' page | Replace Old MIS5 w/ New MIS5 |  | New MIS5 | 1.25 | 1
LTA | MIS6 - Enter lighting Wattage and ballast information on 'Data light kwh' page | Replace Old MIS6 w/ New MIS6 |  | New MIS6 | 1.25 | 1
RetroTypes
LED
T5T8
CFL
Misc

## Data equip kwh (hidden)
Equipment Energy Usage Table
| Total |  |  | full load | Rated | Use load
| Qty. | volts/ | phase | amps | kW | factor | hours/yr | kWh/yr |  | Alternative calculation method
COMPUTER EQUIPMENT
Computer w/ monitor, on 24/7 | 1 |  |  |  | 0.5 | 25% | 8760 | 1095 | Based on LBNL study on computers
Computer w/ CRT monitor | 1 |  |  |  | 0.5 | 25% | 3800 | 475 | Based on LBNL study on computers
Copier - medium size | 1 |  |  |  | 1.4 | 100% | 1200 | 1680 | Source: Guidant custom audit
Desk copier | 1 |  |  |  | 0.85 | 20% | 1200 | 204 | Source: Guidant custom audit
Fax machine | 1 |  |  |  | 0.1 | 10% | 800 | 8 | Source: Guidant custom audit
Printer, Copier | 1 |  |  |  | 0.3 | 50% | 2500 | 375 | Source: Macy's custom audit
Laptop computer | 1 |  |  |  | 0.25 | 25% | 3800 | 237.5
Computer w/ LCD monitor | 1 |  |  |  | 0.35 | 25% | 3800 | 332.5 | Based on LBNL study on computers
Plotter | 1 |  |  |  | 3.5 | 10% | 2000 | 700
Blade server | 1 |  |  |  | 0.4 | 35% | 8760 | 1226.4
c1 | [7 empty] | 0
c2 | [7 empty] | 0
c3 | [7 empty] | 0
c4 | [7 empty] | 0
c5 | [7 empty] | 0
c6 | [7 empty] | 0
c7 | [7 empty] | 0
c8 | [7 empty] | 0
REFRIGERATION EQUIP
Comm refrigerator, solid door | 1 |  |  | 30 | volume, ft3 |  |  | 2909.05 | Source: CEC appliance stds
Refrigerated display, glass door | 1 |  |  | 30 | volume, ft3 |  |  | 3993.1 | Source: CEC appliance stds
Refrigerated display, no door | 1 |  |  | 30 | volume, ft3 |  |  | 4392.41 | Source: CEC appliance stds
Commercial freezer | 1 |  |  | 30 | volume, ft3 |  |  | 5391.05 | Source: CEC appliance stds
Refrig. display, freezer, glass door | 1 |  |  | 30 | volume, ft3 |  |  | 12154.5 | Source: CEC appliance stds
Refrig. display, coffin type freezer | 1 |  |  | 40 | volume, ft3 |  |  | 3365.3 | Source: CEC appliance stds
Beverage vending machine | 1 | [6 empty] | 3573 | Source: CEC data, ave. for listed vending machines
Residential type refrigerator, small | 1 |  |  | 7 | volume, ft2 |  |  | 600.12 | Source: CEC appliance stds
Residential type refrigerator, med | 1 |  |  | 16 | volume, ft3 |  |  | 727.56 | Source: CEC appliance stds
Residential type refrig. w/ice dispenser | 1 |  |  | 22 | volume, ft3 |  |  | 957.32 | Source: CEC appliance stds
Residential type chest freezer | 1 |  |  | 15 | volume, ft3 |  |  | 445.45 | Source: CEC appliance stds
Residential type upright freezer | 1 |  |  | 16 | volume, ft3 |  |  | 803.432 | Source: CEC appliance stds
Frozen yogurt dispenser | 1 | [6 empty] | 3154 | Source: nVidia custom audit
Cold Beverage Dispenser | 1 | 120 | 1 | 4.5 | 0.54 | 25% | 2190 | 1182.6 | webstaurant store
Slush Machine | 1 | 120 | 1 | 12 | 1.44 | 25% | 2190 | 3153.6 | webstaurant store
Ice maker, self contained, small | 1 |  |  | 70 | Harvest Rate(lbs ice/day) |  |  | 3004.68 | Source: CEC appliance stds
Ice maker, self contained, med | 1 |  |  | 150 | Harvest Rate(lbs ice/day) |  |  | 6438.6
Ice maker, self contained, large | 1 |  |  | 300 | Harvest Rate(lbs ice/day) |  |  | 12877.2 | Use actual harvest rate from machine, if avail.
Ice maker, water cooled small | 1 |  |  | 70 | Harvest Rate(lbs ice/day) |  |  | 2330.16
Ice maker, water cooled med | 1 |  |  | 150 | Harvest Rate(lbs ice/day) |  |  | 4993.2
Ice maker, water cooled large | 1 |  |  | 300 | Harvest Rate(lbs ice/day) |  |  | 9986.4
Ice maker, remote Cond. Unit, small | 1 |  |  | 250 | Harvest Rate(lbs ice/day) |  |  | 5584.5
Ice maker, remote Cond. Unit, med | 1 |  |  | 600 | Harvest Rate(lbs ice/day) |  |  | 13402.8
Ice maker, remote Cond. Unit, large | 1 |  |  | 1000 | Harvest Rate(lbs ice/day) |  |  | 22338
WALK IN |  | width | length | height | ft3 | kWh/ft3
Walk in cooler | 1 | 8 | 8 | 10 | 640 | 22.62 | 8760 | 14476.8 | Source: Valley Village analysis by DPR
Walk in freezer | 1 | 8 | 8 | 10 | 640 | 34.978 | 8760 | 22385.9481 | Source: Valley Village analysis by DPR
MISC EQUIPMENT | [7 empty] | 0
KITCHEN EQUIPMENT
Cash register + scale | 1 |  |  |  | 0.05 | 100% | 8760 | 438 | Source: nVidia custom audit
Cash registers | 1 |  |  |  | 0.25 | 30% | 8760 | 657 | Source: Macy's custom audit
Coffee maker | 1 |  |  |  | 1.725 | 20% | 3640 | 1255.8 | Source: nVidia custom audit
Cooler, salad bar | 1 |  |  |  | 1 | 10% | 3640 | 364 | Source: nVidia custom audit
Deep fryer | 1 |  |  |  | 8.64 | 20% | 3640 | 6289.92 | Source: nVidia custom audit
Dishwasher | 1 |  |  |  | 0.25 | 1.25% | 2080 | 6.5 | Insite
Disposal | 1 |  |  |  | 2.4867 | 2% | 3640 | 181.0293 | Source: nVidia custom audit
Kitchen exhaust hood, 4 ft, Type II | 1 |  |  |  | 0.1865 | 100% | 2304 | 429.696 | Type I: for baking ovens and steam
Kitchen exhaust hood, 4 ft, Type I | 1 |  |  |  | 0.746 | 100% | 3456 | 2578.176 | Type II: for open cooking surfaces, grease and smoke
Kitchen exhaust hood, 6-8 ft, Type I | 1 |  |  |  | 1.492 | 100% | 3456 | 5156.352
Kitchen exhaust hood, 8-12 ft, Type I | 1 |  |  |  | 2.238 | 100% | 3456 | 7734.528
Microwave - small | 1 |  |  |  | 0.6 | 100% | 40 | 24 | Source: Regency Plaza custom audit
Mixer, Hobart | 1 |  |  |  | 0.644 | 5% | 3640 | 117.208 | Source: nVidia custom audit
Slicer | 1 |  |  |  | 0.644 | 5% | 3640 | 117.208 | Source: nVidia custom audit
Steamer, rice (large) | 1 |  |  |  | 1.4134 | 20% | 3640 | 1028.9213 | Source: nVidia custom audit
Toaster | 1 |  |  |  | 1.4 | 100% | 20 | 28 | Source: Regency Plaza custom audit
Traulsen glass 2-door salad refrigerator | 1 |  |  |  | 0.99187 | 30% | 8760 | 2606.6475 | Source: nVidia custom audit
Warmer | 1 |  |  |  | 2 | 20% | 3640 | 1456 | Source: nVidia custom audit
Warmer, Glo-Ray | 1 |  |  |  | 0.75 | 40% | 3640 | 1092 | Source: nVidia custom audit
Pizza Oven | 1 |  |  |  | 1.5 | 25% | 2081 |  | webstaurant store
KITCHEN EQUIPMENT | [11 empty] | ft2 | btu | kWh
OTHER | [9 empty] | 2140.625 | BTU/ft2 | 64000 | 137000000 | 40140.6387
Electric hot water heater, 20kW | 1 |  |  |  | 20 | 8% | 8760 | 14016
Electric hot water heater, 40kW | 1 |  |  |  | 40 | 8% | 8760 | 28032
Electric Irons | 1 |  |  |  | 1.5 | 40% | 5000 | 3000 | Source: Macy's custom audit
Elevator, two story | 1 |  |  |  | 16.785 | 50% | 1560 | 13092.3
Other-unknown | 1 |  |  |  | 1 | 11.42% | 8760 | 1000
TVs | 1 |  |  |  | 0.75 | 50% | 5000 | 1875
Typewriter | 1 |  |  |  | 0.2 | 1.25% | 2080 | 5.2
m1 |  |  |  |  | 1.2 | 1.25% | 2081
Kitchen Equip PEPCO
Standard Fat Fryer
Standard Steam Cookers
Standard Hot Food Holding Cabinet (Full-size cabinet)
Standard Hot Food Holding Cabinet (Three-Quarter size cabinet)
Standard Hot Food Holding Cabinet (Half-size cabinet)
Standard Griddles
Standard Combination Ovens
Standard Convection Ovens

## R3 Hist (hidden)
| Energy Usage-Building Energy Use History | [5 empty] | Sect. 3
Pepco
Instructions:
[9 empty] | 1 | Enter elect billing data in chart to lower left - Bill date, number of days, month, kWh and Cost.
[9 empty] | 2 | Enter in chronological order
[9 empty] | 3 | If monthly data is not available, overwrite
[10 empty] | line 53 with totals and leave this sheet out of the printed report. | [5 empty] | Chart table
[9 empty] | 4 | Select electric rate to be used - $.15/kWh default or actual rate calculated from entered costs. |  |  |  |  | month | kWh | Cost | kwh/day
[15 empty] | September | 6 | 1 | 0.2
[15 empty] | October | 6 | 1 | 0.2
[15 empty] | November | 7 | 1 | 0.23333
[10 empty] | Rate used for energy savings: |  |  | Default |  | December | 7 | 1 | 0.23333
[15 empty] | January | 7 | 1 | 0.23333
[15 empty] | February | 7 | 1 | 0.23333
[15 empty] | March | 7 | 1 | 0.23333
[11 empty] | Rates used in energy savings calculations |  |  |  | April | 7 | 1.1 | 0.23333
[12 empty] | kW | kwh |  | May | 7 | 1.1 | 0.23333
[11 empty] | Rate Schedule |  |  |  | June | 7 | 1.1 | 0.23333
[11 empty] | Default | 0 | 0.15 |  | July | 6 | 1 | 0.2
[11 empty] | Actual | 0 | 0.15375 |  | August | 6 | 1 | 0.2
[11 empty] | Other |  |  | if other rate to be used manually enter in box at left.
1
Rate Used
[11 empty] | Default | 0 | 0.15
|  | Actual Demand | Billed Demand | 12 mth peak | Power Factor
|  | Bill date | Days | Month | kWh | Cost | kWh/day
|  |  | 30 | August | 6 | 1 | 0.2
|  |  | 30 | July | 6 | 1 | 0.2
|  |  | 30 | June | 7 | 1.1 | 0.23333
|  |  | 30 | May | 7 | 1.1 | 0.23333
|  |  | 30 | April | 7 | 1.1 | 0.23333
|  |  | 30 | March | 7 | 1 | 0.23333
|  |  | 30 | February | 7 | 1 | 0.23333
|  |  | 30 | January | 7 | 1 | 0.23333
|  |  | 30 | December | 7 | 1 | 0.23333
|  |  | 30 | November | 7 | 1 | 0.23333
|  |  | 30 | October | 6 | 1 | 0.2
|  |  | 30 | September | 6 | 1 | 0.2
|  | Totals | 360 |  | 80 | 12.3 | 0.22222
Your per unit cost of electricity for last 12 mths: |  |  |  | 0.15375 | per kWh
Twelve month billing history
Because the number of days differs throughout in monthly billing data, the monthly profile may be skewed. The chart to the right normalizes the monthly data for usage per day to give a more accurate picture of the yearly load profile.

## printing insert tab1 (hidden)
Dummy Page-replace with insert

## Logos&Administrator Instruction (hidden)
1. replace logos
2. switch utility company name using drop down below in green shaded box
Pepco
PEPCO
Pepco Commercial & Industrial Energy Savings Program
Email: PepcoEnergyEfficiency@LMBPS.com, Web: https://cienergyefficiency.pepco.com/SmallBus.aspx
1-866-353-5798
Copyright © 2012 Potomac Electric Power Company
3. Unhide the relevant Instructions page.
Copyright © 2012 Potomac Electric Power Company
6. hide non-relevant sheets |  | All Rights Reserved
Copyright © 2012 Delmarva Power & Light Company
All Rights Reserved